## Sheet1
Activity ID | Activity Name | Original Duration | Remaining Duration | Start | Finish | Total Float | Predecessor Details | Predecessors
CHI11_WeeklyUpdate_BL1-0_2024-11-15 |  | 530 | 342 | 25-Mar-24 A | 2026-01-22 | 0
Milestones |  | 411 | 328 | 12-Apr-24 A | 2026-01-22 | 0
Div 01 Milestones |  | 362 | 281 | 12-Apr-24 A | 2025-12-04 | 0
General |  | 342 | 261 | 12-Apr-24 A | 2025-11-19 | 2
CHI-11-03-PROP-F | GEN MS- Clayco Proposal Due date | 0 | 0 |  | 12-Apr-24 A |  | CHI11-RFP-10: FF | CHI11-RFP-10
CHI-11-03-MOB-S | GEN MS- GC Mobilization Start | 0 | 0 | 24-Jul-24 A |  |  | CHI11-MOB-10: SS | CHI11-MOB-10
CHI-11-03-EW-S | GEN MS- Earthworks & U/G Utilities Start | 0 | 0 | 19-Aug-24 A |  |  | CHI11-MOB-20: SS, CHI-11-03-MOB-S: SS | CHI11-MOB-20, CHI-11-03-MOB-S
CHI-11-03-PAD-F | GEN MS- Building Footprint Pad Ready | 0 | 0 |  | 04-Sep-24 A |  | CHI-11-03-EW-S: SF, CHI11-MOB-20: FF | CHI-11-03-EW-S, CHI11-MOB-20
CHI-11-03-MOB-F | GEN MS- GC Mobilization Finish/ Site Secured | 0 | 0 |  | 16-Sep-24 A |  | CHI11-MOB-15: FF, CHI-11-03-MOB-S: SF | CHI11-MOB-15, CHI-11-03-MOB-S
CHI-11-03-PSR-F | GEN MS- PSR (Contract) Executed | 0 | 0 |  | 30-Sep-24 A |  | CHI11-RFP-30: FF, CHI-11-03-PROP-F: FS | CHI11-RFP-30, CHI-11-03-PROP-F
CHI-11-03-EW-F | GEN MS- Complete Earthwork & U/G Site Utilities | 0 | 0 |  | 26-Dec-24* | 2 | CHI-11-03-PSR-F: FF, CHI-11-03-MOB-F: FF, CHI11-SU-25: FF, CHI11-SU-40: FF, CHI-11-03-PAD-F: FF | CHI-11-03-PSR-F, CHI-11-03-MOB-F, CHI11-SU-25, CHI11-SU-40, CHI-11-03-PAD-F
CHI-11-03-LHP-F | GEN MS- Complete Landscaping/ Hardscaping | 0 | 0 |  | 2025-11-19 | 2 | CHI11-05-L5-10: FF, CHI11-04-L5-10: FF, CHI11-03-L5-10: FF, CHI-11-03-EW-F: FF | CHI11-05-L5-10, CHI11-04-L5-10, CHI11-03-L5-10, CHI-11-03-EW-F
Admin/ COLO 3 |  | 312 | 231 | 02-Sep-24 A | 2025-10-02 | 0
Core & Shell/ Fitout |  | 153 | 72 | 02-Sep-24 A | 2025-03-15 | 57
CHI-11-03-ROJ-S | Admin/COLO3- Start First ROJ CLAYCO Took over Storage 9/2/2024 | 0 | 0 | 02-Sep-24 A |  |  | CHI-11-03-UPS-01: SS | CHI-11-03-UPS-01
CHI-11-03-FND-S | Admin/COLO3- Start Foundation | 0 | 0 | 19-Sep-24 A |  |  | CHI11-FDN-10: SS, CHI-11-03-EW-S: SS | CHI11-FDN-10, CHI-11-03-EW-S
CHI-11-03-FND-F | Admin/COLO3- Complete Foundation | 0 | 0 |  | 09-Oct-24 A |  | CHI11-FDN-10: FF | CHI11-FDN-10
CHI-11-03-SUP-S | Admin/COLO3- Start Superstructure | 0 | 0 | 14-Oct-24 A |  |  | CHI-11-03-FND-F: FS, CHI11-03-C&S-10: SS | CHI-11-03-FND-F, CHI11-03-C&S-10
CHI-11-03-UGE-F | Admin/COLO3- Complete U/G Utilities/ MV UG Electrical | 0 | 0 |  | 2024-12-14 | 25 | CHI11-03-C&S-20: FF, CHI11-SU-25: FF, CHI11-SU-45: FF | CHI11-03-C&S-20, CHI11-SU-25, CHI11-SU-45
CHI-11-03-SUP-F | Admin/COLO3- Complete Superstructure | 0 | 0 |  | 2024-12-14 | 25 | CHI11-03-C&S-15: FF, CHI-11-03-UGE-F: FF, CHI-11-03-SUP-S: SF | CHI11-03-C&S-15, CHI-11-03-UGE-F, CHI-11-03-SUP-S
CHI-11-03-UGU-F | Admin/COLO3- Complete U/G Utilities (No Elec) | 0 | 0 |  | 2024-12-14 | 25 | CHI11-03-C&S-20: FF, CHI11-SU-20: FF | CHI11-03-C&S-20, CHI11-SU-20
CHI-11-03-SOG-F | Admin/COLO3- Complete SOG | 0 | 0 |  | 2024-12-27 | 15 | CHI-11-03-UGU-F: FF, CHI-11-03-SUP-F: FF, CHI11-03-C&S-35: FF | CHI-11-03-UGU-F, CHI-11-03-SUP-F, CHI11-03-C&S-35
CHI-11-03-DRY-F | Admin/COLO3- Complete Weather Tight | 0 | 0 |  | 16-Jan-25* | 0 | CHI-11-03-SOG-F: FF, CHI11-03-C&S-45: FF | CHI-11-03-SOG-F, CHI11-03-C&S-45
CHI-11-03-ROJ-F | Admin/COLO3- Complete Last ROJ | 0 | 0 |  | 2025-03-08 | 8 | CHI-11-03-TCP-01: SF, CHI-11-03-FND-S: SF, CHI-11-03-ROJ-S: SF | CHI-11-03-TCP-01, CHI-11-03-FND-S, CHI-11-03-ROJ-S
CHI-11-03-GEN-F | Admin/COLO3- Generator Ready for Fuel (Exterior Yard) | 0 | 0 |  | 2025-03-15 | 57 | CHI11-03-YARD-45: FF | CHI11-03-YARD-45
Commissioning |  | 129 | 129 | 2025-04-09 | 2025-09-18 | 0
CHI-11-03-L1CX-S | Admin/COLO3- Start L1 CX | 0 | 0 | 2025-04-09 |  | 38 | CHI11-03-YARD-45: FS, CHI11-03-03-145: FS, CHI11-03-03-245: FS, CHI-11-03-ROJ-F: FS | CHI11-03-YARD-45, CHI11-03-03-145, CHI11-03-03-245, CHI-11-03-ROJ-F
CHI-11-03-L2CX-S | Admin/COLO3- Start L2 CX (Yellow Tag) | 0 | 0 | 2025-05-05 |  | 18 | CHI-11-03-GEN-F: FS, CHI-11-03-L1CX-S: SS, CHI11-03-01-315: SS | CHI-11-03-GEN-F, CHI-11-03-L1CX-S, CHI11-03-01-315
CHI-11-03-POW-F | Admin/COLO3- Complete Utility Power- On | 0 | 0 |  | 2025-05-05 | 33 | CHI-11-03-UGU-F: FF, CHI11-SU-50: SF, CHI-11-03-UGE-F: FF | CHI-11-03-UGU-F, CHI11-SU-50, CHI-11-03-UGE-F
CHI-11-03-L3CX-S | Admin/COLO3- Start L3 CX (Green Tag) | 0 | 0 | 2025-06-04 |  | 13 | CHI11-03-01-320: SS | CHI11-03-01-320
CHI-11-03-L1CX-F | Admin/COLO3- Complete L1 Cx (All Red Tags/ ROJ) | 0 | 0 |  | 2025-06-04 | 57 | CHI11-03-03-305: FF, CHI11-03-04-305: FF, CHI-11-03-L1CX-S: SF | CHI11-03-03-305, CHI11-03-04-305, CHI-11-03-L1CX-S
CHI-11-03-L2CX-F | Admin/COLO3- Complete L2 Cx (Yellow Tag) | 0 | 0 |  | 2025-07-02 | 34 | CHI11-03-03-315: FF, CHI-11-03-L1CX-F: FF, CHI-11-03-L2CX-S: SF | CHI11-03-03-315, CHI-11-03-L1CX-F, CHI-11-03-L2CX-S
CHI-11-03-L3CX-F | Admin/COLO3- Complete CX L3 (Green Tag) | 0 | 0 |  | 14-Aug-25* | 0 | CHI-11-03-BSHVS-F: FF, CHI-11-03-BNM-F: FF, CHI-11-03-BNF-F: FF, CHI11-03-03-305: FF, CHI-11-03-ROJ-F: FF, CHI-11-03-BSA-F: FF, CHI-11-03-BFA-F: FF, CHI-11-03-BRN-F: FF, CHI-11-03-DAS-F: FF, CHI-11-03-BSC-F: FF, CHI-11-03-MOR-F: FF, CHI-11-03-RoIP-F: FF, CHI-11-03-BSL-F: FF, CHI-11-03-BNU-F: FF, CHI-11-03-BNS-F: FF, CHI-11-03-L2CX-F: FF, CHI11-03-03-340: FF, CHI-11-03-BND-F: FF | CHI-11-03-BSHVS-F, CHI-11-03-BNM-F, CHI-11-03-BNF-F, CHI11-03-03-305, CHI-11-03-ROJ-F, CHI-11-03-BSA-F, CHI-11-03-BFA-F, CHI-11-03-BRN-F, CHI-11-03-DAS-F, CHI-11-03-BSC-F, CHI-11-03-MOR-F, CHI-11-03-RoIP-F, CHI-11-03-BSL-F, CHI-11-03-BNU-F, CHI-11-03-BNS-F, CHI-11-03-L2CX-F, CHI11-03-03-340, CHI-11-03-BND-F
CHI-11-03-L4CX-S | Admin/COLO3- Start L4 Cx (Blue Tag) | 0 | 0 | 2025-08-15 |  | 27 | CHI-11-03-L3CX-F: FS, CHI11-03-L4-10: SS, CHI-11-03-L3CX-S: SS | CHI-11-03-L3CX-F, CHI11-03-L4-10, CHI-11-03-L3CX-S
CHI-11-03-L4CX-F | Admin/COLO3- Complete L4 Cx (Blue Tag) | 0 | 0 |  | 2025-09-15 | 3 | CHI11-03-L4-10: FF, CHI-11-03-L4CX-S: SF | CHI11-03-L4-10, CHI-11-03-L4CX-S
CHI-11-03-L5CX-S | Admin/COLO3- Start L5 Cx (White Tag) | 0 | 0 | 2025-09-16 |  | 3 | CHI11-03-L5-10: SS, CHI-11-03-L4CX-S: SS | CHI11-03-L5-10, CHI-11-03-L4CX-S
CHI-11-03-L5CX-F | Admin/COLO3- Cx L5 IST Complete (White Tag) | 0 | 0 |  | 18-Sep-25* | 0 | CHI-11-03-L4CX-F: FF, CHI-11-03-L5CX-S: SF, CHI11-03-L5-10: FF, CHI-11-03-RNI-F: FS | CHI-11-03-L4CX-F, CHI-11-03-L5CX-S, CHI11-03-L5-10, CHI-11-03-RNI-F
Beneficial Use/ TCO |  | 38 | 38 | 2025-08-14 | 2025-10-02 | 0
CHI-11-03-BNU-F | Admin/COLO3- Beneficial Use | 0 | 0 |  | 14-Aug-25* | 0 | CHI11-03-03-340: FF, CHI11-ADMIN-485: FF, CHI11-ADMIN-490: FS | CHI11-03-03-340, CHI11-ADMIN-485, CHI11-ADMIN-490
CHI-11-03-BND-F | Admin/COLO3- Beneficial Use (IDF#1,#2,#3 & #4) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BSA-F | Admin/COLO3- Beneficial Use- Security Operations Center (SOC) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BSL-F | Admin/COLO3- Beneficial Use- Security Low Voltage (SLV) System | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-RoIP-F | Admin/COLO3- Beneficial Use - Radio Over Internet Protocol (RoIP) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-MOR-F | Admin/COLO3- Beneficial Use - Middle of Row (MOR) Cabinets | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BRN-F | Admin/COLO3- Beneficial Use- Regional Network Gateway (RNG) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BNS-F | Admin/COLO3- Beneficial Use - Security Equipment Room (SER) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BFA-F | Admin/COLO3- Beneficial Use- Facilities Operations Center (FOC) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BSC-F | Admin/COLO3- Beneficial Use - Security Corp Cable Rack (SCCR) Cabinets | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-DAS-F | Admin/COLO3- Beneficial Use - Distributed Antenna System (DAS) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BNF-F | Admin/COLO3- Beneficial Use - Facility Cable Room (FCR) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BNM-F | Admin/COLO3- Beneficial Use - Meet Me Room or Entry Rooms (MMR/ER) | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-BSHVS-F | Admin/COLO3- Beneficial Use - Secure & High Value Storage Rooms | 0 | 0 |  | 2025-08-14 | 0 | CHI-11-03-BNU-F: FF | CHI-11-03-BNU-F
CHI-11-03-RNI-F | Admin/COLO3- RNI | 0 | 0 |  | 20-Aug-25* | 0 | CHI-11-03-BNU-F: FS, CHI11-03-03-340: FS 4 | CHI-11-03-BNU-F, CHI11-03-03-340
CHI-11-03-P1ST-F | Admin/COLO3- Phase 1 Security Pre-Testing Complete | 0 | 0 |  | 30-Aug-25* | 0 | CHI-11-03-BNU-F: FF 13 | CHI-11-03-BNU-F
CHI-11-03-EPMS-F | Admin/COLO3- Complete EPMS Testing | 0 | 0 |  | 2025-08-30 | 3 | CHI-11-03-P1ST-F: FF, CHI11-03-04-305: FF, CHI-11-03-BAS-F: FF, CHI-11-03-FIR-F: FF | CHI-11-03-P1ST-F, CHI11-03-04-305, CHI-11-03-BAS-F, CHI-11-03-FIR-F
CHI-11-03-BAS-F | Admin/COLO3- Complete BAS Testing | 0 | 0 |  | 2025-08-30 | 3 | CHI11-03-03-305: FF, CHI-11-03-ROJ-F: FF, CHI-11-03-P1ST-F: FF, CHI11-03-04-280: FF | CHI11-03-03-305, CHI-11-03-ROJ-F, CHI-11-03-P1ST-F, CHI11-03-04-280
CHI-11-03-FIR-F | Admin/COLO3- Complete Fire Alarm | 0 | 0 |  | 2025-08-30 | 3 | CHI-11-03-P1ST-F: FF, CHI11-03-03-305: FF, CHI11-03-03-300: FF | CHI-11-03-P1ST-F, CHI11-03-03-305, CHI11-03-03-300
CHI-11-03-P2ST-F | Admin/COLO3- Phase 2 Security Pre-Testing Complete | 0 | 0 |  | 04-Sep-25* | 0 | CHI-11-03-FIR-F: FF, CHI-11-03-BAS-F: FF, CHI-11-03-EPMS-F: FF, CHI-11-03-P1ST-F: FF 3, CHI-11-03-BNU-F: FF | CHI-11-03-FIR-F, CHI-11-03-BAS-F, CHI-11-03-EPMS-F, CHI-11-03-P1ST-F, CHI-11-03-BNU-F
CHI-11-03-P3ST-F | Admin/COLO3- Phase 3 Security Pre-Testing Complete | 0 | 0 |  | 25-Sep-25* | 0 | CHI-11-03-P2ST-F: FF 17, CHI-11-03-P1ST-F: FF 3 | CHI-11-03-P2ST-F, CHI-11-03-P1ST-F
CHI-11-03-TCO-F | Admin/COLO3- TCO / C of O | 0 | 0 |  | 30-Sep-25* | 0 | CHI-11-03-P3ST-F: FF, CHI-11-03-RNI-F: FF, CHI-11-03-BNU-F: FF, CHI-11-03-L5CX-F: FS 9 | CHI-11-03-P3ST-F, CHI-11-03-RNI-F, CHI-11-03-BNU-F, CHI-11-03-L5CX-F
CHI-11-03-FITOUT-F | Admin/COLO- Admin & COLO3-5 Fitout Complete | 0 | 0 |  | 01-Oct-25* | 0 | CHI11-03-03-305: FF, CHI-11-03-ROJ-F: FF, CHI11-05-03-335: SF 9, CHI11-ADMIN-485: FF, CHI11-03-C&S-45: FF, CHI-11-03-SUP-F: FF | CHI11-03-03-305, CHI-11-03-ROJ-F, CHI11-05-03-335, CHI11-ADMIN-485, CHI11-03-C&S-45, CHI-11-03-SUP-F
CHI-11-03-SC-F | Admin/COLO3- Substantial Completion | 0 | 0 |  | 2025-10-01 | 0 | CHI-11-03-FITOUT-F: FF, CHI-11-03-TCO-F: FF | CHI-11-03-FITOUT-F, CHI-11-03-TCO-F
CHI-11-03-BFN-F | Admin/COLO3- Beneficial Use - All Facility & Network Telecom Access/ Devices etc. | 0 | 0 |  | 01-Oct-25* | 0 | CHI-11-03-SC-F: FF, CHI-11-03-FITOUT-F: FF, CHI-11-03-BNU-F: FF | CHI-11-03-SC-F, CHI-11-03-FITOUT-F, CHI-11-03-BNU-F
CHI-11-03-FC-F | Admin/COLO3- Final Completion/ Turnover to Operations | 0 | 0 |  | 02-Oct-25* | 0 | CHI-11-03-SL-F: FF, CHI-11-03-BFN-F: FF, CHI-11-03-SC-F: FF, CHI-11-03-TCO-F: FF | CHI-11-03-SL-F, CHI-11-03-BFN-F, CHI-11-03-SC-F, CHI-11-03-TCO-F
CHI-11-03-SL-F | Admin/COLO3- Security Lockdown | 0 | 0 |  | 02-Oct-25* | 0 | CHI-11-03-BFN-F: FF 1, CHI-11-03-TCO-F: FF 2 | CHI-11-03-BFN-F, CHI-11-03-TCO-F
COLO 4 |  | 341 | 250 | 02-Sep-24 A | 2025-11-06 | 0
Core & Shell/ Fitout |  | 185 | 94 | 02-Sep-24 A | 2025-04-24 | 53
CHI-11-04-ROJ-S | COLO4- Start First ROJ CLAYCO Took over Storage 9/2/2024 | 0 | 0 | 02-Sep-24 A |  |  | CHI-11-04-UPS-01: SS | CHI-11-04-UPS-01
CHI-11-04-FND-S | COLO4- Foundation Start | 0 | 0 | 19-Sep-24 A |  |  | CHI11-FDN-10: SS 5 | CHI11-FDN-10
CHI-11-04-FND-F | COLO4- Complete Foundation | 0 | 0 |  | 31-Oct-24 A |  | CHI-11-04-FND-S: SF | CHI-11-04-FND-S
CHI-11-04-SUP-S | COLO4- Start Superstructure | 0 | 0 | 01-Nov-24 A |  |  | CHI11-04-C&S-10: SS, CHI-11-04-FND-F: FS | CHI11-04-C&S-10, CHI-11-04-FND-F
CHI-11-04-UGE-F | COLO4- Complete U/G Utilities/ MV UG Electric | 0 | 0 |  | 2024-12-27 | 44 | CHI11-04-C&S-20: FF, CHI11-SU-25: FF, CHI11-SU-45: FF | CHI11-04-C&S-20, CHI11-SU-25, CHI11-SU-45
CHI-11-04-SUP-F | COLO4- Complete Superstructure | 0 | 0 |  | 2024-12-31 | 42 | CHI-11-04-SUP-S: SF, CHI-11-04-UGE-F: FF, CHI11-04-C&S-15: FF | CHI-11-04-SUP-S, CHI-11-04-UGE-F, CHI11-04-C&S-15
CHI-11-04-SOG-F | COLO4- Complete SOG | 0 | 0 |  | 2025-01-10 | 34 | CHI11-04-C&S-30: FF, CHI-11-04-FND-F: FF | CHI11-04-C&S-30, CHI-11-04-FND-F
CHI-11-04-DRY-F | COLO4- Weather Tight | 1 | 1 | 2025-01-30 | 2025-01-30 | 19 | CHI-11-04-SOG-F: FS, CHI-11-04-SUP-F: FS, CHI11-04-C&S-40: FF | CHI-11-04-SOG-F, CHI-11-04-SUP-F, CHI11-04-C&S-40
CHI-11-04-ROJ-F | COLO4- Complete Last ROJ | 0 | 0 |  | 2025-03-30 | 0 | CHI-11-04-TCP-03: FF, CHI-11-04-ROJ-S: SF | CHI-11-04-TCP-03, CHI-11-04-ROJ-S
CHI-11-04-GEN-F | COLO4- Generator Ready for Fuel | 0 | 0 |  | 2025-04-24 | 53 | CHI11-04-YARD-45: FF | CHI11-04-YARD-45
Commissioning |  | 143 | 143 | 2025-04-23 | 2025-10-20 | 0
CHI-11-04-L1CX-S | COLO4- Start L1 CX | 0 | 0 | 2025-04-23 |  | 55 | CHI11-04-03-145: FS, CHI-11-04-ROJ-F: FS | CHI11-04-03-145, CHI-11-04-ROJ-F
CHI-11-04-POW-F | COLO4- Complete Utility Power- On | 0 | 0 |  | 2025-05-05 | 46 | CHI11-SU-50: SF, CHI-11-04-UGE-F: FF | CHI11-SU-50, CHI-11-04-UGE-F
CHI-11-04-L2CX-S | COLO4- Start L2 CX (Yellow Tag) | 0 | 0 | 2025-05-06 |  | 45 | CHI-11-04-GEN-F: FS, CHI-11-04-L1CX-S: SS, CHI11-04-01-315: SS, CHI-11-04-POW-F: FS | CHI-11-04-GEN-F, CHI-11-04-L1CX-S, CHI11-04-01-315, CHI-11-04-POW-F
CHI-11-04-L3CX-S | COLO4- Start L3 CX | 0 | 0 | 2025-06-20 |  | 29 | CHI11-04-01-320: SS | CHI11-04-01-320
CHI-11-04-L1CX-F | COLO4- Complete L1 Cx (All Red Tags/ ROJ) | 0 | 0 |  | 2025-07-19 | 49 | CHI11-04-03-295: FF, CHI11-04-03-305: FF, CHI-11-04-ROJ-F: FF, CHI-11-04-L1CX-S: SF | CHI11-04-03-295, CHI11-04-03-305, CHI-11-04-ROJ-F, CHI-11-04-L1CX-S
CHI-11-04-L2CX-F | COLO4- Complete L2 Cx (Yellow Tag) | 0 | 0 |  | 2025-08-14 | 28 | CHI11-04-04-290: FF, CHI11-04-03-290: FF, CHI11-04-02-295: FF, CHI11-04-01-305: FF, CHI11-04-03-315: FF, CHI-11-04-L1CX-F: FF, CHI-11-04-L2CX-S: SF | CHI11-04-04-290, CHI11-04-03-290, CHI11-04-02-295, CHI11-04-01-305, CHI11-04-03-315, CHI-11-04-L1CX-F, CHI-11-04-L2CX-S
CHI-11-04-L3Cx-F | COLO4- CX L3 Complete | 0 | 0 |  | 19-Sep-25* | 0 | CHI-11-04-BSHVS-F: FF, CHI-11-04-BNM-F: FF, CHI-11-04-BNF-F: FF, CHI-11-04-BFA-F: FF, CHI-11-04-DAS-F: FF, CHI-11-04-RoIP-F: FF, CHI-11-04-BSL-F: FF, CHI-11-04-BSC-F: FF, CHI-11-04-MOR-F: FF, CHI-11-04-L2CX-F: FF, CHI-11-04-L3CX-S: SF, CHI11-04-03-340: FF, CHI-11-04-BND-F: FF | CHI-11-04-BSHVS-F, CHI-11-04-BNM-F, CHI-11-04-BNF-F, CHI-11-04-BFA-F, CHI-11-04-DAS-F, CHI-11-04-RoIP-F, CHI-11-04-BSL-F, CHI-11-04-BSC-F, CHI-11-04-MOR-F, CHI-11-04-L2CX-F, CHI-11-04-L3CX-S, CHI11-04-03-340, CHI-11-04-BND-F
CHI-11-04-L4CX-S | COLO4- Start L4 Cx (Blue Tag) | 0 | 0 | 2025-09-20 |  | 24 | CHI11-04-L4-10: SS, CHI-11-04-L3CX-S: SS | CHI11-04-L4-10, CHI-11-04-L3CX-S
CHI-11-04-L4CX-F | COLO4- Complete L4 Cx (Blue Tag) | 0 | 0 |  | 2025-10-16 | 2 | CHI11-04-L4-10: FF, CHI-11-04-L4CX-S: SF | CHI11-04-L4-10, CHI-11-04-L4CX-S
CHI-11-04-L5CX-S | COLO4- Start L5 Cx (White Tag) | 0 | 0 | 2025-10-17 |  | 2 | CHI11-04-L5-10: SS, CHI-11-04-L4CX-S: SS | CHI11-04-L5-10, CHI-11-04-L4CX-S
CHI-11-04-L5Cx-F | COLO4- Cx L5 IST Complete | 0 | 0 |  | 20-Oct-25* | 0 | CHI-11-04-P2ST-F: FF, CHI-11-04-L4CX-F: FF, CHI-11-04-L5CX-S: SF, CHI11-04-L5-10: FF, CHI-11-04-RNI-F: FS | CHI-11-04-P2ST-F, CHI-11-04-L4CX-F, CHI-11-04-L5CX-S, CHI11-04-L5-10, CHI-11-04-RNI-F
Beneficial Use/ TCO |  | 39 | 39 | 2025-09-19 | 2025-11-06 | 0
CHI-11-04-BND-F | COLO4- Beneficial Use- (IDF#1,#2,#3 & #4) | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-BNU-F | COLO4- Beneficial Use | 0 | 0 |  | 19-Sep-25* | 0 | CHI11-04-03-340: FF, CHI11-03-03-340: FF, CHI-11-04-L3Cx-F: FF | CHI11-04-03-340, CHI11-03-03-340, CHI-11-04-L3Cx-F
CHI-11-04-MOR-F | COLO4- Beneficial Use- Middle of Row (MOR) Cabinets | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-BSC-F | COLO4- Beneficial Use - Security Corp Cable Rack (SCCR) Cabinets | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-BSL-F | COLO4- Beneficial Use - Security Low Voltage (SLV) Systems | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-RoIP-F | COLO4- Beneficial Use- Radio OVer Internet Protocol (RoIP) | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-DAS-F | COLO4- Beneficial Use - Distrbuted Antenna System (DAS) | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-BFA-F | COLO4- Beneficial Use- Facilities Operations Center (FOC) | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-BNF-F | COLO4- Beneficial Use- Facility Cable Room (FCR) | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-BNM-F | COLO4- Beneficial Use- Meet Me Room or Entry Rooms (MMR/ER) | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-BSHVS-F | COLO4- Beneficial Use- Secure & High Value Storage Rooms | 0 | 0 |  | 2025-09-19 | 0 | CHI11-04-03-340: FF | CHI11-04-03-340
CHI-11-04-RNI-F | COLO4- Ready for Network Install | 0 | 0 |  | 24-Sep-25* | 0 | CHI-11-04-BNU-F: FS 4 | CHI-11-04-BNU-F
CHI-11-04-P1ST-F | COLO4- Phase 1 Security Pre-Testing Complete | 0 | 0 |  | 30-Sep-25* | 0 | CHI-11-04-BNU-F: FF 8 | CHI-11-04-BNU-F
CHI-11-04-EPMS-F | COLO4- Complete EPMS Testing | 0 | 0 |  | 2025-09-30 | 4 | CHI-11-04-P1ST-F: FF, CHI-11-04-BAS-F: FF, CHI-11-04-FIR-F: FF | CHI-11-04-P1ST-F, CHI-11-04-BAS-F, CHI-11-04-FIR-F
CHI-11-04-BAS-F | COLO4- Complete BAS Testing | 0 | 0 |  | 2025-09-30 | 4 | CHI11-04-03-300: FF, CHI11-04-03-305: FF, CHI-11-04-ROJ-S: SF, CHI-11-04-ROJ-F: FF, CHI-11-04-P1ST-F: FF, CHI-11-04-GEN-F: FF | CHI11-04-03-300, CHI11-04-03-305, CHI-11-04-ROJ-S, CHI-11-04-ROJ-F, CHI-11-04-P1ST-F, CHI-11-04-GEN-F
CHI-11-04-FIR-F | COLO4- Complete Fire Alarm | 0 | 0 |  | 2025-09-30 | 4 | CHI-11-04-P1ST-F: FF, CHI11-04-03-305: FF, CHI11-04-03-300: FF | CHI-11-04-P1ST-F, CHI11-04-03-305, CHI11-04-03-300
CHI-11-04-P2ST-F | COLO4- Phase 2 Security Pre-Testing Complete | 0 | 0 |  | 04-Oct-25* | 0 | CHI-11-04-EPMS-F: FF, CHI-11-04-P1ST-F: FF 4 | CHI-11-04-EPMS-F, CHI-11-04-P1ST-F
CHI-11-04-P3ST-F | COLO4- Phase 3 Security Pre-Testing Complete | 0 | 0 |  | 23-Oct-25* | 0 | CHI-11-04-P2ST-F: FF 15 | CHI-11-04-P2ST-F
CHI-11-04-TCO-F | COLO4- TCO / C of O | 0 | 0 |  | 29-Oct-25* | 0 | CHI-11-04-P3ST-F: FF, CHI-11-04-BNU-F: FF, CHI-11-04-RNI-F: FF, CHI-11-04-L5Cx-F: FS 8 | CHI-11-04-P3ST-F, CHI-11-04-BNU-F, CHI-11-04-RNI-F, CHI-11-04-L5Cx-F
CHI-11-04-SC-F | COLO4- Substantial Completion | 0 | 0 |  | 2025-10-29 | 7 | CHI-11-04-TCO-F: FF | CHI-11-04-TCO-F
CHI-11-04-FC-F | COLO4- Final Completion/ Turnover to Operations | 0 | 0 |  | 06-Nov-25* | 0 | CHI-11-04-SC-F: FF, CHI-11-04-TCO-F: FF, CHI-11-04-SL-F: FF, CHI-11-03-SC-F: FF, CHI-11-03-TCO-F: FF | CHI-11-04-SC-F, CHI-11-04-TCO-F, CHI-11-04-SL-F, CHI-11-03-SC-F, CHI-11-03-TCO-F
CHI-11-04-SL-F | COLO4- Security Lockdown | 0 | 0 |  | 06-Nov-25* | 0 | CHI-11-04-TCO-F: FF 7, CHI-11-03-TCO-F: FF 2 | CHI-11-04-TCO-F, CHI-11-03-TCO-F
COLO 5 |  | 362 | 259 | 02-Sep-24 A | 2025-12-04 | 0
Core & Shell/ Fitout |  | 214 | 111 | 02-Sep-24 A | 2025-05-31 | 39
CHI-11-05-ROJ-S | COLO5- Start First ROJ - CLAYCO Took over Storage 9/2/2024 | 0 | 0 | 02-Sep-24 A |  |  | CHI-11-04-ROJ-S: SS, CHI-11-05-UPS-01: SS | CHI-11-04-ROJ-S, CHI-11-05-UPS-01
CHI-11-05-FND-S | COLO5- Foundation Start | 0 | 0 | 19-Sep-24 A |  |  | CHI-11-05-ROJ-S: SS, CHI11-FDN-10: SS | CHI-11-05-ROJ-S, CHI11-FDN-10
CHI-11-05-SUP-S | COLO5- Start Superstructure | 0 | 0 | 12-Nov-24 A |  |  | CHI11-05-C&S-10: SS | CHI11-05-C&S-10
CHI-11-05-FND-F | COLO5- Complete Foundation | 0 | 0 |  | 12-Nov-24 A |  | CHI11-FDN-15: FF, CHI-11-05-FND-S: SF | CHI11-FDN-15, CHI-11-05-FND-S
CHI-11-05-UGE-F | COLO5- Complete U/G Utilities/ MV UG Electric | 0 | 0 |  | 2025-01-13 | 61 | CHI11-05-C&S-20: FF, CHI11-SU-45: FF, CHI11-SU-25: FF | CHI11-05-C&S-20, CHI11-SU-45, CHI11-SU-25
CHI-11-05-SUP-F | COLO5- Complete Superstructure | 0 | 0 |  | 2025-01-15 | 59 | CHI-11-05-SUP-S: SF, CHI-11-05-UGE-F: FF, CHI11-05-C&S-15: FF | CHI-11-05-SUP-S, CHI-11-05-UGE-F, CHI11-05-C&S-15
CHI-11-05-SOG-F | COLO5- Complete SOG | 0 | 0 |  | 2025-01-25 | 51 | CHI-11-05-UGE-F: FF, CHI11-05-C&S-30: FF, CHI-11-05-FND-F: FF | CHI-11-05-UGE-F, CHI11-05-C&S-30, CHI-11-05-FND-F
CHI-11-05-DRY-F | Weather Tight - Entire Building | 0 | 0 |  | 2025-02-14 | 35 | CHI-11-05-SUP-F: FF, CHI-11-05-SOG-F: FF, CHI11-05-C&S-35: FS | CHI-11-05-SUP-F, CHI-11-05-SOG-F, CHI11-05-C&S-35
CHI-11-05-ROJ-F | COLO5- Complete Last ROJ | 0 | 0 |  | 2025-03-31 | 79 | CHI-11-05-TCP-01: SF, CHI-11-05-ROJ-S: SF | CHI-11-05-TCP-01, CHI-11-05-ROJ-S
CHI-11-05-GEN-F | COLO5- Generator Ready for Fuel | 0 | 0 |  | 2025-05-31 | 39 | CHI11-05-YARD-55: FF | CHI11-05-YARD-55
Commissioning |  | 170 | 170 | 2025-04-21 | 2025-11-19 | 0
CHI-11-05-L1CX-S | COLO5- Start L1 CX | 0 | 0 | 2025-04-21 |  | 72 | CHI11-05-01-145: SS, CHI-11-05-ROJ-F: FS | CHI11-05-01-145, CHI-11-05-ROJ-F
CHI-11-05-POW-F | COLO5- Complete Utility Power- On | 0 | 0 |  | 2025-05-05 | 61 | CHI11-SU-50: SF, CHI-11-05-UGE-F: FF | CHI11-SU-50, CHI-11-05-UGE-F
CHI-11-05-L2CX-S | COLO5- Start L2 CX (Yellow Tag) | 0 | 0 | 2025-06-05 |  | 36 | CHI-11-05-GEN-F: FS, CHI-11-05-L1CX-S: SS, CHI-11-05-POW-F: FS, CHI11-05-01-315: SS | CHI-11-05-GEN-F, CHI-11-05-L1CX-S, CHI-11-05-POW-F, CHI11-05-01-315
CHI-11-05-L3CX-S | COLO5- Start L3 CX | 0 | 0 | 2025-07-19 |  | 68 | CHI11-05-04-295: FS, CHI11-05-03-290: FS, CHI11-05-02-295: FS, CHI11-05-01-305: FS, CHI-11-05-L2CX-S: SS, CHI11-05-01-320: SS | CHI11-05-04-295, CHI11-05-03-290, CHI11-05-02-295, CHI11-05-01-305, CHI-11-05-L2CX-S, CHI11-05-01-320
CHI-11-05-L1CX-F | COLO5- Complete L1 Cx (All Red Tags/ ROJ) | 0 | 0 |  | 2025-08-05 | 54 | CHI11-05-03-295: FF, CHI11-05-03-305: FF, CHI-11-05-ROJ-F: FF, CHI-11-05-L1CX-S: SF | CHI11-05-03-295, CHI11-05-03-305, CHI-11-05-ROJ-F, CHI-11-05-L1CX-S
CHI-11-05-L2CX-F | COLO5- Complete L2 Cx (Yellow Tag) | 0 | 0 |  | 2025-09-03 | 31 | CHI11-05-04-295: FF, CHI11-05-03-290: FF, CHI11-05-02-295: FF, CHI11-05-01-305: FF, CHI11-05-03-315: FF, CHI-11-05-L1CX-F: FF, CHI-11-05-L2CX-S: SF | CHI11-05-04-295, CHI11-05-03-290, CHI11-05-02-295, CHI11-05-01-305, CHI11-05-03-315, CHI-11-05-L1CX-F, CHI-11-05-L2CX-S
CHI-11-05-L3CX-F | COLO5- CX Level 3 Complete | 0 | 0 |  | 11-Oct-25* | 0 | CHI-11-05-BSHVS-F: FS, CHI-11-05-BNM-F: FS, CHI-11-05-BNF-F: FS, CHI-11-05-L3CX-S: SF, CHI-11-05-L2CX-F: FF, CHI11-05-01-340: FF, CHI11-05-02-340: FF, CHI11-05-04-340: FF, CHI-11-05-DAS-F: FS, CHI-11-05-RoIP-F: FS, CHI-11-05-BSL-F: FS, CHI-11-05-BSC-F: FS, CHI-11-05-BMOR-F: FS, CHI-11-05-BND-F: FS, CHI11-05-03-340: FF | CHI-11-05-BSHVS-F, CHI-11-05-BNM-F, CHI-11-05-BNF-F, CHI-11-05-L3CX-S, CHI-11-05-L2CX-F, CHI11-05-01-340, CHI11-05-02-340, CHI11-05-04-340, CHI-11-05-DAS-F, CHI-11-05-RoIP-F, CHI-11-05-BSL-F, CHI-11-05-BSC-F, CHI-11-05-BMOR-F, CHI-11-05-BND-F, CHI11-05-03-340
CHI-11-05-L4CX-S | COLO5- Start L4 Cx (Blue Tag) | 0 | 0 | 2025-10-17 |  | 27 | CHI11-05-L4-10: SS, CHI-11-05-L3CX-S: SS | CHI11-05-L4-10, CHI-11-05-L3CX-S
CHI-11-05-L4CX-F | COLO5- Complete L4 Cx (Blue Tag) | 0 | 0 |  | 2025-11-15 | 3 | CHI11-05-L4-10: FF, CHI-11-05-L4CX-S: SF | CHI11-05-L4-10, CHI-11-05-L4CX-S
CHI-11-05-L5CX-S | COLO5- Start L5 Cx (White Tag) | 0 | 0 | 2025-11-17 |  | 3 | CHI11-05-L5-10: SS, CHI-11-05-L4CX-S: SS | CHI11-05-L5-10, CHI-11-05-L4CX-S
CHI-11-05-L5CX-F | COLO5- Cx Level 5 IST Complete | 0 | 0 |  | 19-Nov-25* | 0 | CHI-11-05-L4CX-F: FF, CHI-11-05-L5CX-S: SF, CHI11-05-L5-10: FF, CHI-11-05-RNI-F: FS | CHI-11-05-L4CX-F, CHI-11-05-L5CX-S, CHI11-05-L5-10, CHI-11-05-RNI-F
Beneficial Use/ TCO |  | 42 | 42 | 2025-10-11 | 2025-12-04 | 0
CHI-11-05-BND-F | COLO5- Beneficial Use (IDF#1,#2,#3 & #4) | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-BNU-F | COLO5- Beneficial Use | 0 | 0 |  | 11-Oct-25* | 0 | CHI11-05-01-340: FS, CHI11-05-02-340: FS, CHI11-05-03-340: FS, CHI11-05-04-340: FS | CHI11-05-01-340, CHI11-05-02-340, CHI11-05-03-340, CHI11-05-04-340
CHI-11-05-BMOR-F | COLO5- Beneficial Use- Middle of Row (MOR) Cabinets | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-BSC-F | COLO5- Beneficial Use - Security Corp Cable Rack (SCCR) Cabinets | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-BSL-F | COLO5- Beneficial Use - Security Low Voltage (SLV) System | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-RoIP-F | COLO5- Beneficial Use- Radio Over Internet Protocol (RoIP) | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-DAS-F | COLO5- Beneficial Use - Distributed Antenna System (DAS) | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-BNF-F | COLO5- Beneficial Use Facility Cable Room (FCR) | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-BNM-F | COLO5- Beneficial Use Meet Me Room or Entry Rooms (MMR/ER) | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-BSHVS-F | COLO5- Beneficial Use Secure & High Value Storage Rooms | 0 | 0 |  | 2025-10-11 | 0 | CHI-11-05-BNU-F: FF | CHI-11-05-BNU-F
CHI-11-05-RNI-F | COLO5- Ready for Network Install | 0 | 0 |  | 17-Oct-25* | 0 | CHI11-05-03-340: FF 5, CHI11-05-04-340: FF 1, CHI-11-05-BNU-F: FF | CHI11-05-03-340, CHI11-05-04-340, CHI-11-05-BNU-F
CHI-11-05-P1ST-F | COLO5- Phase 1 Security Pre-Testing Complete | 0 | 0 |  | 31-Oct-25* | 0 | CHI-11-05-BNU-F: FF 16 | CHI-11-05-BNU-F
CHI-11-05-EPMS-F | COLO5- Complete EPMS Testing | 0 | 0 |  | 2025-10-31 | 2 | CHI-11-05-P1ST-F: FF, CHI-11-05-BAS-F: FF, CHI-11-05-FIR-F: FF | CHI-11-05-P1ST-F, CHI-11-05-BAS-F, CHI-11-05-FIR-F
CHI-11-05-BAS-F | COLO5- Complete BAS Testing | 0 | 0 |  | 2025-10-31 | 2 | CHI-11-05-P1ST-F: FF, CHI-11-05-GEN-F: FF | CHI-11-05-P1ST-F, CHI-11-05-GEN-F
CHI-11-05-FIR-F | COLO5- Complete Fire Alarm | 0 | 0 |  | 2025-10-31 | 2 | CHI-11-05-P1ST-F: FF | CHI-11-05-P1ST-F
CHI-11-05-P2ST-F | COLO5- Phase 2 Security Pre-Testing Complete | 0 | 0 |  | 03-Nov-25* | 0 | CHI-11-05-FIR-F: FF, CHI-11-05-BAS-F: FF, CHI-11-05-EPMS-F: FF, CHI-11-05-P1ST-F: FF 2 | CHI-11-05-FIR-F, CHI-11-05-BAS-F, CHI-11-05-EPMS-F, CHI-11-05-P1ST-F
CHI-11-05-P3ST-F | COLO5- Phase 3 Security Pre-Testing Complete | 0 | 0 |  | 26-Nov-25* | 0 | CHI-11-05-P2ST-F: FF 19, CHI-11-05-BNU-F: FF | CHI-11-05-P2ST-F, CHI-11-05-BNU-F
CHI-11-05-TCO-F | COLO5- TCO / C of O | 0 | 0 |  | 02-Dec-25* | 0 | CHI-11-03-FITOUT-F: FS, CHI-11-03-LHP-F: FF 7, CHI-11-05-L5CX-F: FS 9 | CHI-11-03-FITOUT-F, CHI-11-03-LHP-F, CHI-11-05-L5CX-F
CHI-11-05-SC-F | COLO5- Substantial Completion | 0 | 0 |  | 2025-12-02 | 0 | CHI-11-05-TCO-F: FF, CHI11-05-03-340: FF, CHI11-05-04-340: FF, CHI-11-05-P3ST-F: FF, CHI-11-05-DAS-F: FF, CHI-11-05-RoIP-F: FF, CHI-11-05-BSL-F: FF, CHI-11-05-BSC-F: FF | CHI-11-05-TCO-F, CHI11-05-03-340, CHI11-05-04-340, CHI-11-05-P3ST-F, CHI-11-05-DAS-F, CHI-11-05-RoIP-F, CHI-11-05-BSL-F, CHI-11-05-BSC-F
CHI-11-05-FC-F | COLO5- Final Completion/Turnover to Operations | 0 | 0 |  | 04-Dec-25* | 0 | CHI-11-05-TCO-F: FF, CHI-11-05-SL-F: FF | CHI-11-05-TCO-F, CHI-11-05-SL-F
CHI-11-05-SL-F | COLO5- Secuirty Lockdown | 0 | 0 |  | 04-Dec-25* | 0 | CHI-11-05-TCO-F: FF 2, CHI-11-05-SC-F: FF 2 | CHI-11-05-TCO-F, CHI-11-05-SC-F
Clayco Key Milestones |  | 411 | 328 | 19-Aug-24 A | 2026-01-22 | 0
CHI-11-MS-01 | CHI11: Construction Start | 0 | 0 | 19-Aug-24 A |  |  | CHI11-MOB-10: SS, CHI11-MOB-20: SS | CHI11-MOB-10, CHI11-MOB-20
CHI-11-MS-02 | CHI11: Building Pad Ready | 0 | 0 |  | 04-Sep-24 A |  | CHI11-MOB-20: FF, CHI-11-MS-01: SF | CHI11-MOB-20, CHI-11-MS-01
CHI-11-MS-04 | CHI11: Structure Start | 0 | 0 | 14-Oct-24 A |  |  | CHI11-03-C&S-10: SS | CHI11-03-C&S-10
CHI-11-MS-03 | CHI11: Foundations Complete | 0 | 0 |  | 12-Nov-24 A |  | CHI11-FDN-15: FF, CHI-11-MS-02: FF | CHI11-FDN-15, CHI-11-MS-02
CHI-11-MS-05 | CHI11: Structure Complete | 0 | 0 |  | 2024-12-03 | 40 | CHI-11-MS-04: SF, CHI-11-MS-03: FF, CHI11-03-C&S-10: FF, CHI11-04-C&S-10: FF, CHI11-05-C&S-10: FF | CHI-11-MS-04, CHI-11-MS-03, CHI11-03-C&S-10, CHI11-04-C&S-10, CHI11-05-C&S-10
CHI-11-MS-06 | CHI11: Utilities Available to Owner (Gas Service N/A) | 0 | 0 |  | 2024-12-26 | 135 | CHI11-SU-40: FF | CHI11-SU-40
CHI-11-MS-08 | CHI11: Enclosure Complete | 0 | 0 |  | 2025-01-15 | 43 | CHI-11-MS-05: FF, CHI-11-MS-07: FF, CHI11-05-C&S-15: FF | CHI-11-MS-05, CHI-11-MS-07, CHI11-05-C&S-15
CHI-11-MS-07 | CHI11: Roofing Complete | 0 | 0 |  | 2025-01-15 | 43 | CHI11-05-C&S-15: FF | CHI11-05-C&S-15
CHI-11-MS-09 | CHI11: Electrical Service Available | 0 | 0 |  | 2025-05-05 | 208 | CHI11-SU-50: SF | CHI11-SU-50
CHI-11-MS-10 | CHI11: Commissioning Complete | 0 | 0 |  | 2025-11-19 | 49 | CHI-11-05-L5CX-F: FF, CHI-11-MS-06: FF, CHI-11-MS-09: FF | CHI-11-05-L5CX-F, CHI-11-MS-06, CHI-11-MS-09
CHI-11-MS-11 | CHI11: Substantial Completion | 0 | 0 |  | 2025-12-02 | 0 | CHI-11-05-TCO-F: FF | CHI-11-05-TCO-F
CHI-11-MS-12 | CHI11: Final Completion (SC+40d) | 0 | 0 |  | 2026-01-22 | 0 | CHI-11-MS-11: FF 40 | CHI-11-MS-11
CHI-11-MS-13 | CHI11: Closeout Complete | 0 | 0 |  | 2026-01-22 | 0 | CHI-11-MS-10: FF, CHI-11-05-FC-F: FF, CHI-11-05-L3CX-F: FF, CHI-11-04-FC-F: FF, CHI-11-03-FC-F: FF, CHI-11-CFCI-15: FF, CHI-11-MS-11: FF, CHI-11-MS-12: FF | CHI-11-MS-10, CHI-11-05-FC-F, CHI-11-05-L3CX-F, CHI-11-04-FC-F, CHI-11-03-FC-F, CHI-11-CFCI-15, CHI-11-MS-11, CHI-11-MS-12
Preconstruction |  | 161 | 30 | 25-Mar-24 A | 2024-12-23 | 48
RFP / PSR |  | 151 | 0 | 25-Mar-24 A | 30-Sep-24 A
CHI11-RFP-10 | RFP- RFP Issued (Revised 3.21.24) and Proposal Due to MSFT | 16 | 0 | 25-Mar-24 A | 12-Apr-24 A
CHI11-RFP-15 | RFP- Microsoft Reviews Proposals | 15 | 0 | 15-Apr-24 A | 03-May-24 A |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI11-RFP-20 | RFP- Microsoft Awards CHI11 | 5 | 0 | 06-May-24 A | 05-Jun-24 A |  | CHI11-RFP-15: FS | CHI11-RFP-15
CHI11-RFP-25 | RFP- PSR Executed (Early Works) | 1 | 0 | 06-Jun-24 A | 06-Jun-24 A |  | CHI11-RFP-20: FS | CHI11-RFP-20
CHI11-RFP-30 | RFP- PSR Executed (Full GMP) | 1 | 0 | 30-Sep-24 A | 30-Sep-24 A |  | CHI11-RFP-25: FS 90, CHI11-PROC-15: FF | CHI11-RFP-25, CHI11-PROC-15
BIM |  | 70 | 30 | 18-Jul-24 A | 2024-12-23 | 48
CHI11-BIM-10 | BIM- BIM Kickoff | 0 | 0 | 18-Jul-24 A |  |  | CHI11-PROC-10: SS 20 | CHI11-PROC-10
CHI11-BIM-15 | BIM- UG BIM Co-ordination | 25 | 0 | 19-Jul-24 A | 26-Sep-24 A |  | CHI11-BIM-10: FS | CHI11-BIM-10
CHI11-BIM-20 | BIM- Above ground BIM Co-ordination | 30 | 30 | 27-Sep-24 A | 2024-12-23 | 48 | CHI11-BIM-15: FS | CHI11-BIM-15
Procurement |  | 399 | 295 | 09-Apr-24 A | 2025-11-21 | 47
Early Awards |  | 60 | 0 | 07-Jun-24 A | 30-Sep-24 A
CHI11-PROC-10 | PROCUREMENT- ARL & Subcontractor Awards | 60 | 0 | 07-Jun-24 A | 07-Sep-24 A |  | CHI11-RFP-25: FS | CHI11-RFP-25
CHI11-PROC-15 | PROCUREMENT- Buyouts & Early Procurement | 60 | 0 | 07-Jun-24 A | 30-Sep-24 A |  | CHI11-RFP-25: FS | CHI11-RFP-25
MSFT OFCI ROJ Dates |  | 247 | 176 | 09-Apr-24 A | 2025-05-15 | 52
COLO 3 |  | 184 | 113 | 09-Apr-24 A | 2025-03-13 | 45
Busway / Busplugs |  | 166 | 5 | 09-Apr-24 A | 2025-02-23 | 42
CHI-11-03-BUS-01 | Admin/C03- OFCI- Receive Busway / Busplugs (Starline Holding) (Del Date- 1/25/24) | 0 | 0 | 09-Apr-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-BUS-02 | Admin/C03- OFCI- Busway / Busplugs (Starline Holding) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 42 | CHI-11-03-BUS-01: SS, CHI11-03-01-135: FS | CHI-11-03-BUS-01, CHI11-03-01-135
CHI-11-03-BUS-03 | Admin/C03- OFCI- Busway / Busplugs (Starline Holding) Delivered | 0 | 0 |  | 2025-02-23 | 42 | CHI-11-03-BUS-02: FF | CHI-11-03-BUS-02
PEMB Procurement (1st Del) |  | 23 | 0 | 14-Oct-24 A | 14-Oct-24 A
CHI-11-03-PEMB-01 | Admin/C03-5- OFCI- Receive PEMB Procurement (1st Del) (Nucor) (SOW Del Date-10/3/24) | 0 | 0 | 14-Oct-24 A |  |  | CHI11-RFP-25: SS | CHI11-RFP-25
CHI-11-03-PEMB-02 | Admin/C03-5- OFCI- PEMB Procurement (1st Del) (Nucor) Shipping/ ROJ | 5 | 0 | 14-Oct-24 A | 14-Oct-24 A |  | CHI11-03-C&S-10: SS, CHI-11-03-PEMB-01: FS | CHI11-03-C&S-10, CHI-11-03-PEMB-01
CHI-11-03-PEMB-03 | Admin/C03-5- OFCI- PEMB Procurement (1st Del) (Nucor) Delivered | 0 | 0 |  | 14-Oct-24 A |  | CHI-11-03-PEMB-02: FF | CHI-11-03-PEMB-02
LV Switchgear |  | 5 | 5 | 2025-02-28 | 2025-03-04 | 5
CHI-11-03-LVS-01 | Admin/C03- OFCI- Receive LV Switchgear (LVS) (Eaton) (SOW Del Date- 2/28/25) | 0 | 0 | 28-Feb-25* |  | 5 | CHI-11-03-FND-S: SS | CHI-11-03-FND-S
CHI-11-03-LVS-02 | Admin/C03- OFCI- LV Switchgear (LVS) (Eaton) Shipping/ ROJ | 5 | 5 | 2025-02-28 | 2025-03-04 | 5 | CHI-11-03-LVS-01: FS, CHI11-03-01-135: FS | CHI-11-03-LVS-01, CHI11-03-01-135
CHI-11-03-LVS-03 | Admin/C03- OFCI- LV Switchgear (LVS) (Eaton) Delivered | 0 | 0 |  | 2025-03-04 | 5 | CHI-11-03-LVS-02: FS | CHI-11-03-LVS-02
Automatic Transfer Switches |  | 95 | 95 | 2024-11-15 | 2025-02-23 | 14
CHI-11-03-ATS-01 | Admin/C03- OFCI- Receive Automatic Transfer Switches (ATS) (Schneider) (SOW Del Date- 4/30/24) | 0 | 0 | 15-Nov-24* |  | 104 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-ATS-02 | Admin/C03- OFCI- Automatic Transfer Switches (ATS) (Schneider) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 14 | CHI-11-03-ATS-01: SS, CHI11-03-01-135: FS | CHI-11-03-ATS-01, CHI11-03-01-135
CHI-11-03-ATS-03 | Admin/C03- OFCI- Automatic Transfer Switches (ATS) (Schneider) Delivered | 0 | 0 |  | 2025-02-23 | 14 | CHI-11-03-ATS-02: FS | CHI-11-03-ATS-02
Elec Performance Monitoring System |  | 95 | 95 | 2024-11-15 | 2025-02-23 | 14
CHI-11-03-EPMS-01 | Admin/C03- OFCI- Receive Elec. Performance Monitoring System (EPMS) (Schneider) (SOW Del Date- 4/30/24) | 0 | 0 | 15-Nov-24* |  | 104 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-EPMS-02 | Admin/C03- OFCI- Elec. Performance Monitoring System (EPMS) (Schneider) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 14 | CHI-11-03-EPMS-01: SS, CHI11-03-01-135: FS | CHI-11-03-EPMS-01, CHI11-03-01-135
CHI-11-03-EPMS-03 | Admin/C03- OFCI- Elec. Performance Monitoring System (EPMS) (Schneider) Delivered | 0 | 0 |  | 2025-02-23 | 14 | CHI-11-03-EPMS-02: FF | CHI-11-03-EPMS-02
Power Distribution Units |  | 95 | 95 | 2024-11-15 | 2025-02-23 | 54
CHI-11-03-PDU-01 | Admin/C03- OFCI- Receive Power Distribution Units (PDU) (ABB) (SOW Del Date- 4/30/24) | 0 | 0 | 15-Nov-24* |  | 144 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-PDU-02 | Admin/C03- OFCI- Power Distribution Units (PDU) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 54 | CHI-11-03-PDU-01: FS, CHI11-03-01-135: FS | CHI-11-03-PDU-01, CHI11-03-01-135
CHI-11-03-PDU-03 | Admin/C03- OFCI- Power Distribution Units (PDU) Delivered | 0 | 0 |  | 2025-02-23 | 54 | CHI-11-03-PDU-02: FF | CHI-11-03-PDU-02
Air Handling Units |  | 184 | 5 | 09-Oct-24 A | 2025-03-13 | 31
CHI-11-03-AHU-01 | Admin/C03- OFCI- Receive Air Handling Units (AHU) (Stulz) (SOW Del Date- 9/04/24) | 0 | 0 | 09-Oct-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-AHU-02 | Admin/C03- OFCI- Air Handling Units (AHU) (Stulz) Shipped/ROJ | 5 | 5 | 2025-03-09 | 2025-03-13 | 31 | CHI11-03-01-245: FF, CHI-11-03-AHU-01: SS | CHI11-03-01-245, CHI-11-03-AHU-01
CHI-11-03-AHU-03 | Admin/C03- OFCI- Air Handling Units (AHU) (Stulz) Delivered | 0 | 0 |  | 2025-03-13 | 31 | CHI-11-03-AHU-02: FS | CHI-11-03-AHU-02
Packaged Diesel Generator Set |  | 96 | 96 | 2024-11-15 | 2025-02-24 | 53
CHI-11-03-GEN-01 | Admin/C03- OFCI- Receive Packaged Diesel Generator Set (CAT Holt) (SOW Del Date- 5/14/24) | 0 | 0 | 15-Nov-24* |  | 144 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-GEN-02 | Admin/C03- OFCI- Packaged Diesel Generator Set (CAT Holt) Shipping/ ROJ | 5 | 5 | 2025-02-20 | 2025-02-24 | 53 | CHI11-03-YARD-25: SS, CHI-11-03-GEN-01: FS | CHI11-03-YARD-25, CHI-11-03-GEN-01
CHI-11-03-GEN-03 | Admin/C03- OFCI- Packaged Diesel Generator Set (CAT Holt) Delivered | 0 | 0 |  | 2025-02-24 | 53 | CHI-11-03-GEN-02: FS | CHI-11-03-GEN-02
HAC/Racking |  | 93 | 93 | 2024-11-15 | 2025-02-21 | 16
CHI-11-03-HAC-01 | Admin/C03- OFCI- Receive HAC/Racking (Tate Access) (SOW Del Date- 5/17/24) | 0 | 0 | 15-Nov-24* |  | 106 | CHI11-RFP-25: SS | CHI11-RFP-25
CHI-11-03-HAC-02 | Admin/C03- OFCI- HAC/Racking (Tate Access) Shipping/ ROJ | 3 | 3 | 2025-02-19 | 2025-02-21 | 16 | CHI-11-03-HAC-01: FS, CHI11-03-01-135: FS | CHI-11-03-HAC-01, CHI11-03-01-135
CHI-11-03-HAC-03 | Admin/C03- OFCI- HAC/Racking (Tate Access) Delivered | 0 | 0 |  | 2025-02-21 | 16 | CHI-11-03-HAC-02: FF | CHI-11-03-HAC-02
Medium Voltage Switchgear |  | 166 | 5 | 15-Oct-24 A | 2025-02-23 | 54
CHI-11-03-MVS-01 | Admin/C03- OFCI- Receive Medium Voltage Switchgear (JDC Power Sys) (SOW Del Date- 7/30/24) | 0 | 0 | 15-Oct-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-MVS-02 | Admin/C03- OFCI- Medium Voltage Switchgear (MVS) (JD Power Sys) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 54 | CHI-11-03-MVS-01: FS, CHI11-03-01-135: FS | CHI-11-03-MVS-01, CHI11-03-01-135
CHI-11-03-MVS-03 | Admin/C03- OFCI- Medium Voltage Switchgear (MVS) (JD Power Sys) Delivered | 0 | 0 |  | 2025-02-23 | 54 | CHI-11-03-MVS-02: FF | CHI-11-03-MVS-02
UPS System W / Battery |  | 166 | 5 | 02-Sep-24 A | 2025-02-23 | 14
CHI-11-03-UPS-01 | Admin/C03- OFCI- Received SUB Warehouse 9/28/2023 UPS System w/ Battery (UPS) (Eaton) (SOW Del Date- 8/13/23) | 0 | 0 | 02-Sep-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-UPS-02 | Admin/C03- OFCI- UPS System w/ Battery (UPS) (Eaton) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 14 | CHI-11-03-UPS-01: FS, CHI11-03-01-135: FS | CHI-11-03-UPS-01, CHI11-03-01-135
CHI-11-03-UPS-03 | Admin/C03- OFCI- UPS System w/ Battery (UPS) (Eaton) Delivered | 0 | 0 |  | 2025-02-23 | 14 | CHI-11-03-UPS-02: FF | CHI-11-03-UPS-02
Building Automation System |  | 82 | 82 | 2024-11-30 | 2025-02-23 | 63
CHI-11-03-BAS-01 | Admin/C03- OFCI- Receive Building Automation System (BAS) (Automated Logic Corp) (SOW Del Date- 11/28/24) | 0 | 0 | 30-Nov-24* |  | 140 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-BAS-02 | Admin/C03- OFCI- Building Automation System (BAS) (ALC) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 63 | CHI-11-03-BAS-01: SS, CHI11-03-01-135: FS | CHI-11-03-BAS-01, CHI11-03-01-135
CHI-11-03-BAS-03 | Admin/C03- OFCI- Building Automation System (BAS) (ALC) Delivered | 0 | 0 |  | 2025-02-23 | 63 | CHI-11-03-BAS-02: FS | CHI-11-03-BAS-02
Auto Transfer Control Panel |  | 1 | 1 | 2025-03-08 | 2025-03-08 | 1
CHI-11-03-TCP-01 | Admin/C03- OFCI- Receive Auto Transfer Control Panel (TCP) (Del Date- 3/8/2025) | 0 | 0 | 08-Mar-25* |  | 1 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-TCP-02 | Admin/C03- OFCI- Auto Transfer Control Panel (TCP) Shipping/ ROJ | 1 | 1 | 2025-03-08 | 2025-03-08 | 1 | CHI-11-03-TCP-01: SS, CHI11-03-01-135: FS | CHI-11-03-TCP-01, CHI11-03-01-135
CHI-11-03-TCP-03 | Admin/C03- OFCI- Auto Transfer Control Panel (TCP) Delivered | 0 | 0 |  | 2025-03-08 | 1 | CHI-11-03-TCP-02: FF | CHI-11-03-TCP-02
Auxillary Power Distribution |  | 1 | 1 | 2025-03-08 | 2025-03-08 | 1
CHI-11-03-ADP-01 | Admin/C03- OFCI- Receive Auxillary (Mech) Power Distribution Panels (ADP) (Del Date- 3/8/2025) | 0 | 0 | 08-Mar-25* |  | 1 | CHI11-03-03-15: FS, CHI11-RFP-10: FS | CHI11-03-03-15, CHI11-RFP-10
CHI-11-03-ADP-02 | Admin/C03- OFCI- Auxillary (Mech) Power Distribution Panels (ADP) Shipping/ ROJ | 1 | 1 | 2025-03-08 | 2025-03-08 | 1 | CHI-11-03-ADP-01: SS, CHI11-03-01-135: FS | CHI-11-03-ADP-01, CHI11-03-01-135
CHI-11-03-ADP-03 | Admin/C03- OFCI- Auxillary (Mech) Power Distribution Panels (ADP) Delivered | 0 | 0 |  | 2025-03-08 | 1 | CHI-11-03-ADP-02: FS | CHI-11-03-ADP-02
Utility Pad Mount Switchgear |  | 115 | 10 | 23-Oct-24 A | 2025-02-28 | 49
CHI-11-03-UPM-01 | Admin/C03- OFCI- Receive Utility Pad Mount Switchgear (Del Date- 7/30/2024) | 0 | 0 | 23-Oct-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-UPM-02 | Admin/C03- OFCI- Utility Pad Mount Switchgear (UPM) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 49 | CHI-11-03-UPM-01: FS, CHI11-03-01-135: FS | CHI-11-03-UPM-01, CHI11-03-01-135
CHI-11-03-UPM-03 | Admin/C03- OFCI- Utility Pad Mount Switchgear (UPM) Delivered | 5 | 5 | 2025-02-24 | 2025-02-28 | 49 | CHI-11-03-UPM-02: FS | CHI-11-03-UPM-02
Pad Mounted Transformers |  | 95 | 95 | 2024-11-15 | 2025-02-23 | 54
CHI-11-03-XFM-01 | Admin/C03- OFCI- Receive Pad Mounted Transformers (XFM-TX) (Del Date- 7/30/2024) | 0 | 0 | 15-Nov-24* |  | 144 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-XFM-02 | Admin/C03- OFCI- Pad Mounted Transformers (XFM-TX) Shipping/ ROJ | 5 | 5 | 2025-02-19 | 2025-02-23 | 54 | CHI-11-03-XFM-01: FS, CHI11-03-01-135: FS | CHI-11-03-XFM-01, CHI11-03-01-135
CHI-11-03-XFM-03 | Admin/C03- OFCI- Pad Mounted Transformers (XFM-TX) Delivered | 0 | 0 |  | 2025-02-23 | 54 | CHI-11-03-XFM-02: FF | CHI-11-03-XFM-02
Main LV Switch Board |  | 1 | 1 | 2025-03-08 | 2025-03-08 | 1
CHI-11-03-MSB-01 | Admin/C03- OFCI- Receive Main LV Switch Board (MSB) (SOW Del Date- 3/8/2025) | 0 | 0 | 08-Mar-25* |  | 1 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-03-MSB-02 | Admin/C03- OFCI- Main LV Switch Board (MSB) Shipping/ ROJ | 1 | 1 | 2025-03-08 | 2025-03-08 | 1 | CHI-11-03-MSB-01: FS, CHI11-03-01-135: FS | CHI-11-03-MSB-01, CHI11-03-01-135
CHI-11-03-MSB-03 | Admin/C03- OFCI- Main LV Switch Board (MSB) Delivered | 0 | 0 |  | 2025-03-08 | 1 | CHI-11-03-MSB-02: FF | CHI-11-03-MSB-02
COLO 4 |  | 212 | 141 | 02-Sep-24 A | 2025-04-10 | 38
Busway / Busplugs |  | 130 | 130 | 2024-11-15 | 2025-03-30 | 37
CHI-11-04-BUS-01 | C04- OFCI- Receive Busway / Busplugs (BSW) (Starline Holding) (SOW Del Date- 2/23/24) | 0 | 0 | 15-Nov-24* |  | 162 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-BUS-02 | C04- OFCI- Busway / Busplugs (BSW) (Starline Holding) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 37 | CHI11-04-01-160: FS, CHI-11-04-BUS-01: SS | CHI11-04-01-160, CHI-11-04-BUS-01
CHI-11-04-BUS-03 | C04- OFCI- Busway / Busplugs (BSW) (Starline Holding) Delivered | 0 | 0 |  | 2025-03-30 | 37 | CHI-11-04-BUS-02: FF | CHI-11-04-BUS-02
LV Switchgear |  | 3 | 3 | 2025-02-28 | 2025-03-02 | 28
CHI-11-04-LVS-01 | C04- OFCI- Receive LV Switchgear (Eaton) (SOW Del Date- 2/28/25) | 0 | 0 | 28-Feb-25* |  | 28 | CHI11-RFP-10: SS | CHI11-RFP-10
CHI-11-04-LVS-02 | C04- OFCI- LV Switchgear (Eaton) Shipping/ROJ | 3 | 3 | 2025-02-28 | 2025-03-02 | 28 | CHI-11-04-LVS-01: SS | CHI-11-04-LVS-01
CHI-11-04-LVS-03 | C04- OFCI- LV Switchgear (Eaton) Delivered | 0 | 0 |  | 2025-03-02 | 28 | CHI-11-04-LVS-02: FF | CHI-11-04-LVS-02
Automatic Transfer Switches |  | 130 | 130 | 2024-11-15 | 2025-03-30 | 0
CHI-11-04-ATS-01 | C04- OFCI- Receive Automatic Transfer Switches (ATS) (Schneider) (SOW Del Date- 6/30/24) | 0 | 0 | 2024-11-15 |  | 125 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-ATS-02 | C04- OFCI- Automatic Transfer Switches (ATS) (Schneider) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 0 | CHI11-04-01-160: FS, CHI-11-04-ATS-01: SS | CHI11-04-01-160, CHI-11-04-ATS-01
CHI-11-04-ATS-03 | C04- OFCI- Automatic Transfer Switches (ATS) (Schneider) Delivered | 0 | 0 |  | 2025-03-30 | 0 | CHI-11-04-ATS-02: FF | CHI-11-04-ATS-02
Elec Performance Monitoring System |  | 130 | 130 | 2024-11-15 | 2025-03-30 | 0
CHI-11-04-EPMS-01 | C04- OFCI- Receive Elec. Performance Monitoring Syst. (EPMS) (EPMS) (Schneider) (SOW Del Date- 6/30/24) | 0 | 0 | 15-Nov-24* |  | 125 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-EPMS-02 | C04- OFCI- Elec. Performance Monitoring Syst. (EPMS) (EPMS) (Schneider) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 0 | CHI11-04-01-160: FS, CHI-11-04-EPMS-01: SS | CHI11-04-01-160, CHI-11-04-EPMS-01
CHI-11-04-EPMS-03 | C04- OFCI- Elec. Performance Monitoring Syst. (EPMS) (EPMS) (Schneider) Delivered | 0 | 0 |  | 2025-03-30 | 0 | CHI-11-04-EPMS-02: FF | CHI-11-04-EPMS-02
Power Distribution Units |  | 130 | 130 | 2024-11-15 | 2025-03-30 | 49
CHI-11-04-PDU-01 | C04- OFCI- Reveive Power Distribution Units (PDU) (ABB) (SOW Del Date- 7/12/24) | 0 | 0 | 15-Nov-24* |  | 174 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-PDU-02 | C04- OFCI- Power Distribution Units (PDU) (ABB) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 49 | CHI11-04-01-160: FS, CHI-11-04-PDU-01: SS | CHI11-04-01-160, CHI-11-04-PDU-01
CHI-11-04-PDU-03 | C04- OFCI- Power Distribution Units (PDU) (ABB) Delivered | 0 | 0 |  | 2025-03-30 | 49 | CHI-11-04-PDU-02: FF | CHI-11-04-PDU-02
Air Handling Units |  | 203 | 5 | 30-Sep-24 A | 2025-04-05 | 37
CHI-11-04-AHU-01 | C04- OFCI- Receive Air Handling Units (AHU) (Stulz) (SOW Del Date- 9/9/24) | 0 | 0 | 30-Sep-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-AHU-02 | C04- OFCI- Air Handling Units (AHU) (Stulz) Shipping/ ROJ | 5 | 5 | 2025-04-01 | 2025-04-05 | 37 | CHI11-04-01-230: FF, CHI-11-04-AHU-01: FS | CHI11-04-01-230, CHI-11-04-AHU-01
CHI-11-04-AHU-03 | C04- OFCI- Air Handling Units (AHU) (Stulz) Delivered | 0 | 0 |  | 2025-04-05 | 37 | CHI-11-04-AHU-02: FS | CHI-11-04-AHU-02
Packaged Diesel Generator Set |  | 141 | 141 | 2024-11-15 | 2025-04-10 | 33
CHI-11-04-GEN-01 | C04- OFCI- Receive Packaged Diesel Generator Set (GEN) (CAT Holt) (SOW Del Date- 6/4/24) | 0 | 0 | 15-Nov-24* |  | 169 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-GEN-02 | C04- OFCI- Packaged Diesel Generator Set (GEN) (CAT Holt) Shipping/ROJ | 5 | 5 | 2025-04-06 | 2025-04-10 | 33 | CHI11-04-YARD-25: FS, CHI-11-04-GEN-01: SS | CHI11-04-YARD-25, CHI-11-04-GEN-01
CHI-11-04-GEN-03 | C04- OFCI- Packaged Diesel Generator Set (GEN) (CAT Holt) Delivered | 0 | 0 |  | 2025-04-10 | 33 | CHI-11-04-GEN-02: FF | CHI-11-04-GEN-02
HAC/Racking |  | 128 | 128 | 2024-11-15 | 2025-03-28 | 37
CHI-11-04-HAC-01 | C04- OFCI- Receive HAC/Racking (Tate Access) (SOW Del Date- 6/18/24) | 0 | 0 | 15-Nov-24* |  | 162 | CHI11-RFP-25: SS | CHI11-RFP-25
CHI-11-04-HAC-02 | C04- OFCI- HAC/Racking (Tate Access) Shipping/ROJ | 3 | 3 | 2025-03-26 | 2025-03-28 | 37 | CHI11-04-01-160: FS, CHI-11-04-HAC-01: SS | CHI11-04-01-160, CHI-11-04-HAC-01
CHI-11-04-HAC-03 | C04- OFCI- HAC/Racking (Tate Access) Delivered | 0 | 0 |  | 2025-03-28 | 37 | CHI-11-04-HAC-02: FF | CHI-11-04-HAC-02
Medium Voltage Switchgear |  | 201 | 5 | 23-Oct-24 A | 2025-03-30 | 44
CHI-11-04-MVS-01 | C04- OFCI- Receive Medium Voltage Switchgear (JDC Power Sys) (SOW Del Date- 8/30/24) | 0 | 0 | 23-Oct-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-MVS-02 | C04- OFCI- Medium Voltage Switchgear (JDC Power Sys) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 44 | CHI11-04-01-160: FS, CHI-11-04-MVS-01: SS | CHI11-04-01-160, CHI-11-04-MVS-01
CHI-11-04-MVS-03 | C04- OFCI- Medium Voltage Switchgear (JDC Power Sys) Delivered | 0 | 0 |  | 2025-03-30 | 44 | CHI-11-04-MVS-02: FF | CHI-11-04-MVS-02
UPS System W / Battery |  | 201 | 5 | 02-Sep-24 A | 2025-03-30 | 0
CHI-11-04-UPS-01 | C04- OFCI- Received SUB Warehouse 11/23/2023 Static UPS System W/Batt (UPS) (Eaton) (SOW Del Date- 11/11/23) | 0 | 0 | 02-Sep-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-UPS-02 | C04- OFCI- Static UPS System W/Batt (UPS) (Eaton) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 0 | CHI11-04-01-160: FS, CHI-11-04-UPS-01: SS | CHI11-04-01-160, CHI-11-04-UPS-01
CHI-11-04-UPS-03 | C04- OFCI- Static UPS System W/Batt (UPS) (Eaton) Delivered | 0 | 0 |  | 2025-03-30 | 0 | CHI-11-04-UPS-02: FF | CHI-11-04-UPS-02
Building Automation System |  | 5 | 5 | 2024-12-29 | 2025-01-04 | 130
CHI-11-04-BAS-01 | C04- OFCI- Receive Building Automation System (BAS) (Automated Logic Corp) (SOW Del Date- 12/29/24) | 0 | 0 | 29-Dec-24* |  | 130 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-BAS-02 | C04- OFCI- Building Automation System (BAS) (Automated Logic Corp) Shipping/ROJ | 5 | 5 | 2024-12-29 | 2025-01-04 | 130 | CHI-11-04-BAS-01: SS | CHI-11-04-BAS-01
CHI-11-04-BAS-03 | C04- OFCI- Building Automation System (BAS) (Automated Logic Corp) Delivered | 0 | 0 |  | 2025-01-04 | 130 | CHI-11-04-BAS-02: FF | CHI-11-04-BAS-02
Auto Transfer Control Panel |  | 1 | 1 | 2025-03-30 | 2025-03-30 | 0
CHI-11-04-TCP-01 | C04- OFCI- Receive Auto Transfer Control Panel (TCP) (Del Date-3/30/2025) | 0 | 0 | 30-Mar-25* |  | 0 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-TCP-02 | C04- OFCI- Auto Transfer Control Panel (TCP) Shipping/ROJ | 1 | 1 | 2025-03-30 | 2025-03-30 | 0 | CHI-11-04-TCP-01: SS | CHI-11-04-TCP-01
CHI-11-04-TCP-03 | C04- OFCI- Auto Transfer Control Panel (TCP) Delivered | 0 | 0 |  | 2025-03-30 | 0 | CHI-11-04-TCP-02: FF | CHI-11-04-TCP-02
Auxillary Power Distribution |  | 1 | 1 | 2025-03-30 | 2025-03-30 | 0
CHI-11-04-ADP-01 | C04- OFCI- Receive Mech Power Distribution Panels (ADP) (Del Date 3/30/2025) | 0 | 0 | 30-Mar-25* |  | 0 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-ADP-02 | C04- OFCI- Mech Power Distribution Panels (ADP) Shipping/ROJ | 1 | 1 | 2025-03-30 | 2025-03-30 | 0 | CHI-11-04-ADP-01: SS | CHI-11-04-ADP-01
CHI-11-04-ADP-03 | C04- OFCI- Mech Power Distribution Panels (ADP) Delivered | 0 | 0 |  | 2025-03-30 | 0 | CHI-11-04-ADP-02: FF | CHI-11-04-ADP-02
Utility Pad Mount Switchgear |  | 145 | 5 | 23-Oct-24 A | 2025-03-30 | 44
CHI-11-04-UPM-01 | C04- OFCI- Receive Utility Pad Mount Switchgear (UPM) (Del Date 8/30/2024) | 0 | 0 | 23-Oct-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-UPM-02 | C04- OFCI- Utility Pad Mount Switchgear (UPM) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 44 | CHI11-04-01-160: FS, CHI-11-04-UPM-01: SS | CHI11-04-01-160, CHI-11-04-UPM-01
CHI-11-04-UPM-03 | C04- OFCI- Utility Pad Mount Switchgear (UPM) Delivered | 0 | 0 |  | 2025-03-30 | 44 | CHI-11-04-UPM-02: FF | CHI-11-04-UPM-02
Pad Mounted Transformers |  | 130 | 130 | 2024-11-15 | 2025-03-30 | 44
CHI-11-04-XFM-01 | C04- OFCI- Reveive Pad Mounted Transformers (XMF) (Del Date 8/30/2024) | 0 | 0 | 15-Nov-24* |  | 169 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-XFM-02 | C04- OFCI- Pad Mounted Transformers (XMF) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 44 | CHI11-04-01-160: FS, CHI-11-04-XFM-01: SS | CHI11-04-01-160, CHI-11-04-XFM-01
CHI-11-04-XFM-03 | C04- OFCI- Pad Mounted Transformers (XMF) Delivered | 0 | 0 |  | 2025-03-30 | 44 | CHI-11-04-XFM-02: FF | CHI-11-04-XFM-02
Main LV Switch Board |  | 1 | 1 | 2025-03-30 | 2025-03-30 | 0
CHI-11-04-MSB-01 | C04- OFCI- Receive Main LV Switch Board (MSB) (Del Date 3/30/2025) | 0 | 0 | 30-Mar-25* |  | 0 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-04-MSB-02 | C04- OFCI- Main LV Switch Board (MSB) Shipping/ROJ | 1 | 1 | 2025-03-30 | 2025-03-30 | 0 | CHI-11-04-MSB-01: SS | CHI-11-04-MSB-01
CHI-11-04-MSB-03 | C04- OFCI- Main LV Switch Board (MSB) Delivered | 0 | 0 |  | 2025-03-30 | 0 | CHI-11-04-MSB-02: FF | CHI-11-04-MSB-02
COLO 5 |  | 247 | 176 | 02-Sep-24 A | 2025-05-15 | 52
Busway / Busplugs |  | 164 | 164 | 2024-11-15 | 2025-05-03 | 30
CHI-11-05-BUS-01 | C05- OFCI- Receive Busway / Busplugs (BSW) (Starline Holding) (SOW Del Date- 4/23/24) | 0 | 0 | 15-Nov-24* |  | 189 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-BUS-02 | C05- OFCI- Busway / Busplugs (BSW) (Starline Holding) Shipping/ROJ | 5 | 5 | 2025-04-29 | 2025-05-03 | 30 | CHI11-05-01-165: FS, CHI-11-05-BUS-01: SS | CHI11-05-01-165, CHI-11-05-BUS-01
CHI-11-05-BUS-03 | C05- OFCI- Busway / Busplugs (BSW) (Starline Holding) Delivered | 0 | 0 |  | 2025-05-03 | 30 | CHI-11-05-BUS-02: FF | CHI-11-05-BUS-02
LV Switchgear |  | 5 | 5 | 2025-03-30 | 2025-04-03 | 17
CHI-11-05-LVS-01 | C05- OFCI- Receive LV Switchgear (Eaton) (SOW Del Date- 3/30/25) | 0 | 0 | 30-Mar-25* |  | 17 | CHI11-RFP-10: SS | CHI11-RFP-10
CHI-11-05-LVS-02 | C05- OFCI- LV Switchgear (Eaton) Shipping/ROJ | 5 | 5 | 2025-03-30 | 2025-04-03 | 17 | CHI-11-05-LVS-01: SS | CHI-11-05-LVS-01
CHI-11-05-LVS-03 | C05- OFCI- LV Switchgear (Eaton) Delivered | 0 | 0 |  | 2025-04-03 | 17 | CHI-11-05-LVS-02: FF | CHI-11-05-LVS-02
Automatic Transfer Switches |  | 151 | 151 | 2024-11-15 | 2025-04-20 | 0
CHI-11-05-ATS-01 | C05- OFCI- Receive Automatic Transfer Switches (ATS) (Schneider) (SOW Del Date- 8/31/24) | 0 | 0 | 15-Nov-24* |  | 150 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-ATS-02 | C05- OFCI- Automatic Transfer Switches (ATS) (Schneider) Shipping/ROJ | 1 | 1 | 2025-04-20 | 2025-04-20 | 0 | CHI11-05-01-140: FS, CHI-11-05-ATS-01: SS | CHI11-05-01-140, CHI-11-05-ATS-01
CHI-11-05-ATS-03 | C05- OFCI- Automatic Transfer Switches (ATS) (Schneider) Delivered | 0 | 0 |  | 2025-04-20 | 0 | CHI-11-05-ATS-02: FF | CHI-11-05-ATS-02
Elec Performance Monitoring System |  | 151 | 151 | 2024-11-15 | 2025-04-20 | 0
CHI-11-05-EPMS-01 | C05- OFCI- Receive Elec. Performance Monitoring Syst. (EPMS) (Schneider) (SOW Del Date- 8/31/24) | 0 | 0 | 15-Nov-24* |  | 150 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-EPMS-02 | C05- OFCI- Elec. Performance Monitoring Syst. (EPMS) (Schneider) Shipping/ROJ | 1 | 1 | 2025-04-20 | 2025-04-20 | 0 | CHI11-05-01-140: FS, CHI-11-05-EPMS-01: SS | CHI11-05-01-140, CHI-11-05-EPMS-01
CHI-11-05-EPMS-03 | C05- OFCI- Elec. Performance Monitoring Syst. (EPMS) (Schneider) Delivered | 0 | 0 |  | 2025-04-20 | 0 | CHI-11-05-EPMS-02: FF | CHI-11-05-EPMS-02
Power Distribution Units |  | 168 | 168 | 2024-11-15 | 2025-05-07 | 39
CHI-11-05-PDU-01 | C05- OFCI- Receive Power Distribution Units (PDU) (ABB) (SOW Del Date- 9/30/24) | 0 | 0 | 15-Nov-24* |  | 202 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-PDU-02 | C05- OFCI- Power Distribution Units (PDU) (ABB) Shipping/ROJ | 5 | 5 | 2025-05-03 | 2025-05-07 | 39 | CHI11-05-01-180: FF, CHI-11-05-PDU-01: SS | CHI11-05-01-180, CHI-11-05-PDU-01
CHI-11-05-PDU-03 | C05- OFCI- Power Distribution Units (PDU) (ABB) Delivered | 0 | 0 |  | 2025-05-07 | 39 | CHI-11-05-PDU-02: FF | CHI-11-05-PDU-02
Air Handling Units |  | 232 | 1 | 12-Sep-24 A | 2025-05-11 | 28
CHI-11-05-AHU-01 | C05- OFCI- Receive Air Handling Units (AHU) (Stulz) (SOW Del Date- 9/16/24) | 0 | 0 | 12-Sep-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-AHU-02 | C05- OFCI- Air Handling Units (AHU) (Stulz) Shipping/ROJ | 1 | 1 | 2025-05-11 | 2025-05-11 | 28 | CHI11-05-01-235: FS, CHI-11-05-AHU-01: SS | CHI11-05-01-235, CHI-11-05-AHU-01
CHI-11-05-AHU-03 | C05- OFCI- Air Handling Units (AHU) (Stulz) Delivered | 0 | 0 |  | 2025-05-11 | 28 | CHI-11-05-AHU-02: FF | CHI-11-05-AHU-02
Packaged Diesel Generator Set |  | 176 | 176 | 2024-11-15 | 2025-05-15 | 52
CHI-11-05-GEN-01 | C05- OFCI- Receive Packaged Diesel Generator Set (GPC) (CAT Holt) (SOW Del Date- 6/26/24) | 0 | 0 | 15-Nov-24* |  | 223 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-GEN-02 | C05- OFCI- Packaged Diesel Generator Set (GPC) (CAT Holt) Shipping/ROJ | 5 | 5 | 2025-05-11 | 2025-05-15 | 52 | CHI11-05-YARD-25: FS, CHI-11-05-GEN-01: SS | CHI11-05-YARD-25, CHI-11-05-GEN-01
CHI-11-05-GEN-03 | C05- OFCI- Packaged Diesel Generator Set (GPC) (CAT Holt) Delivered | 0 | 0 |  | 2025-05-15 | 52 | CHI-11-05-GEN-02: FF | CHI-11-05-GEN-02
HAC/Racking |  | 159 | 159 | 2024-11-15 | 2025-04-28 | 33
CHI-11-05-HAC-01 | C05- OFCI- Receive HAC/Racking (Tate Access) (SOW Del Date- 7/3/24) | 0 | 0 | 15-Nov-24* |  | 188 | CHI11-RFP-25: SS | CHI11-RFP-25
CHI-11-05-HAC-02 | C05- OFCI- HAC/Racking (Tate Access) Shipping/ROJ | 4 | 4 | 2025-04-25 | 2025-04-28 | 33 | CHI11-05-01-165: FF, CHI-11-05-HAC-01: SS | CHI11-05-01-165, CHI-11-05-HAC-01
CHI-11-05-HAC-03 | C05- OFCI- HAC/Racking (Tate Access) Delivered | 0 | 0 |  | 2025-04-28 | 33 | CHI-11-05-HAC-02: FF | CHI-11-05-HAC-02
Medium Voltage Switchgear |  | 180 | 5 | 30-Oct-24 A | 2025-05-03 | 62
CHI-11-05-MVS-01 | C05- OFCI- Receive Medium Voltage Switchgear (MVS) (JDC Power Sys) (SOW Del Date- 10/30/24) | 0 | 0 | 30-Oct-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-MVS-02 | C05- OFCI- Medium Voltage Switchgear (MVS) (JDC Power Sys) Shipping/ROJ | 5 | 5 | 2025-04-29 | 2025-05-03 | 62 | CHI11-05-01-165: FS, CHI-11-05-MVS-01: SS | CHI11-05-01-165, CHI-11-05-MVS-01
CHI-11-05-MVS-03 | C05- OFCI- Medium Voltage Switchgear (MVS) (JDC Power Sys) Delivered | 0 | 0 |  | 2025-05-03 | 62 | CHI-11-05-MVS-02: FF | CHI-11-05-MVS-02
UPS System W / Battery |  | 201 | 5 | 02-Sep-24 A | 2025-03-30 | 21
CHI-11-05-UPS-01 | C05- OFCI- Received SUB Warehouse 12/28/2023 Static UPS System W/Batt (UPS) (Eaton) (SOW Del Date- 12/11/23) | 0 | 0 | 02-Sep-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-UPS-02 | C05- OFCI- Static UPS System W/Batt (UPS) (Eaton) Shipping/ROJ | 5 | 5 | 2025-03-26 | 2025-03-30 | 21 | CHI11-04-01-160: FS, CHI-11-05-UPS-01: SS | CHI11-04-01-160, CHI-11-05-UPS-01
CHI-11-05-UPS-03 | C05- OFCI- Static UPS System W/Batt (UPS) (Eaton) Delivered | 0 | 0 |  | 2025-03-30 | 21 | CHI-11-05-UPS-02: FF | CHI-11-05-UPS-02
Auto Transfer Control Panel |  | 5 | 5 | 2025-03-30 | 2025-04-04 | 17
CHI-11-05-TCP-01 | C05- OFCI- Receive Auto Transfer Control Panel (TCP) (Del Date 3/30/2025) | 0 | 0 | 30-Mar-25* |  | 17 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-TCP-02 | C05- OFCI- Auto Transfer Control Panel (TCP) Shipping/ROJ | 5 | 5 | 2025-03-30 | 2025-04-04 | 17 | CHI-11-05-TCP-01: SS | CHI-11-05-TCP-01
CHI-11-05-TCP-03 | C05- OFCI- Auto Transfer Control Panel (TCP) Delivered | 0 | 0 |  | 2025-04-04 | 17 | CHI-11-05-TCP-02: FF | CHI-11-05-TCP-02
Building Automation System |  | 5 | 5 | 2025-01-28 | 2025-02-02 | 129
CHI-11-05-BAS-01 | C05- OFCI- Receive Building Automation System (BAS) (Automated Logic Corp) (SOW Del Date- 1/28/25) | 0 | 0 | 28-Jan-25* |  | 129 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-BAS-02 | C05- OFCI- Building Automation System (BAS) (Automated Logic Corp) Shipping/ROJ | 5 | 5 | 2025-01-28 | 2025-02-02 | 129 | CHI-11-05-BAS-01: SS | CHI-11-05-BAS-01
CHI-11-05-BAS-03 | C05- OFCI- Building Automation System (BAS) (Automated Logic Corp) Delivered | 0 | 0 |  | 2025-02-02 | 129 | CHI-11-05-BAS-02: FF | CHI-11-05-BAS-02
Auxillary Power Distribution |  | 5 | 5 | 2025-03-30 | 2025-04-04 | 17
CHI-11-05-ADP-01 | C05- OFCI- Receive Mech Power Distribution Panels (ADP) (Del Date 3/30/2025) | 0 | 0 | 30-Mar-25* |  | 17 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-ADP-02 | C05- OFCI- Mech Power Distribution Panels (ADP) Shipping/ROJ | 5 | 5 | 2025-03-30 | 2025-04-04 | 17 | CHI-11-05-ADP-01: SS | CHI-11-05-ADP-01
CHI-11-05-ADP-03 | C05- OFCI- Mech Power Distribution Panels (ADP) Delivered | 0 | 0 |  | 2025-04-04 | 17 | CHI-11-05-ADP-02: FF | CHI-11-05-ADP-02
Utility Pad Mount Switchgear |  | 179 | 5 | 23-Oct-24 A | 2025-05-03 | 58
CHI-11-05-UPM-01 | C05- OFCI- Receive Utility Pad Mount Switchgear (UPM) (Del Date 10/30/2024) | 0 | 0 | 23-Oct-24 A |  |  | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-UPM-02 | C05- OFCI- Utility Pad Mount Switchgear (UPM) Shipping/ROJ | 5 | 5 | 2025-04-29 | 2025-05-03 | 58 | CHI11-05-01-165: FS, CHI-11-05-UPM-01: FS | CHI11-05-01-165, CHI-11-05-UPM-01
CHI-11-05-UPM-03 | C05- OFCI- Utility Pad Mount Switchgear (UPM) Delivered | 0 | 0 |  | 2025-05-03 | 58 | CHI-11-05-UPM-02: FF | CHI-11-05-UPM-02
Pad Mounted Transformers |  | 164 | 164 | 2024-11-15 | 2025-05-03 | 56
CHI-11-05-XFM-01 | C05- OFCI- Receive Pad Mounted Transformers (XMF) (Del Date 10/30/2024) | 0 | 0 | 15-Nov-24* |  | 215 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-XFM-02 | C05- OFCI- Pad Mounted Transformers (XMF) Shipping/ROJ | 5 | 5 | 2025-04-29 | 2025-05-03 | 56 | CHI11-05-01-165: FS, CHI-11-05-XFM-01: SS | CHI11-05-01-165, CHI-11-05-XFM-01
CHI-11-05-XFM-03 | C05- OFCI- Pad Mounted Transformers (XMF) Delivered | 0 | 0 |  | 2025-05-03 | 56 | CHI-11-05-XFM-02: FF | CHI-11-05-XFM-02
Main LV Switch Board |  | 5 | 5 | 2025-03-30 | 2025-04-04 | 17
CHI-11-05-MSB-01 | C05- OFCI- Receive Main LV Switch Board (MSB) (Del Date 3/30/2025) | 0 | 0 | 30-Mar-25* |  | 17 | CHI11-RFP-10: FS | CHI11-RFP-10
CHI-11-05-MSB-02 | C05- OFCI- Main LV Switch Board (MSB) Shipping/ROJ | 5 | 5 | 2025-03-30 | 2025-04-04 | 17 | CHI-11-05-MSB-01: SS | CHI-11-05-MSB-01
CHI-11-05-MSB-03 | C05- OFCI- Main LV Switch Board (MSB) Delivered | 0 | 0 |  | 2025-04-04 | 17 | CHI-11-05-MSB-02: FF | CHI-11-05-MSB-02
CFCI (Critical Only) |  | 455 | 363 | 07-Aug-24 A | 2025-11-21 | 56
CHI-11-CFCI-10 | CFCI- MV Metering Cabinet - Substitute [43 Weeks] | 301 | 209 | 07-Aug-24 A | 2025-06-18 | 9 | CHI11-PROC-10: SS | CHI11-PROC-10
CHI-11-CFCI-15 | CFCI- MV Metering Cabinet - *Not Used* [65 Weeks] - Not Tied | 455 | 363 | 07-Aug-24 A | 2025-11-21 | 56 | CHI11-PROC-10: SS | CHI11-PROC-10
CHI-11-CFCI-20 | CFCI- MV Cables Fabrication/ Lead Time | 244 | 155 | 17-Aug-24 A | 2025-04-24 | 5 | CHI11-BIM-15: SS 15, CHI11-PROC-10: SS | CHI11-BIM-15, CHI11-PROC-10
CHI-11-CFCI-25 | CFCI- Cable Bus Fabrication/ Lead Time | 103 | 103 | 2024-11-15 | 2025-03-03 | 57 | CHI11-BIM-20: SS 26 | CHI11-BIM-20
CHI-11-CFCI-30 | CFCI- HACs Fabrication/ Lead Time | 19 | 19 | 2024-11-15 | 2024-12-05 | 115 | CHI-11-CFCI-25: SS, CHI11-BIM-20: SS 26 | CHI-11-CFCI-25, CHI11-BIM-20
Construction |  | 385 | 293 | 24-Jul-24 A | 2025-11-19 | 0
Site Prep/ Mobilization |  | 34 | 0 | 24-Jul-24 A | 16-Sep-24 A
CHI11-MOB-10 | Site Mobilization | 0 | 0 | 24-Jul-24 A |  |  | CHI11-RFP-25: SS | CHI11-RFP-25
CHI11-MOB-15 | Set-Up Trailers & Install Temp Utilities | 12 | 0 | 25-Jul-24 A | 16-Sep-24 A |  | CHI11-MOB-10: FS | CHI11-MOB-10
CHI11-MOB-20 | Fine Grading Building Pad | 13 | 0 | 19-Aug-24 A | 04-Sep-24 A |  | CHI11-MOB-15: SS 19 | CHI11-MOB-15
Site Utilities |  | 182 | 134 | 08-Oct-24 A | 2025-05-05 | 33
Overall |  | 178 | 134 | 08-Oct-24 A | 2025-05-05 | 33
CHI11-SU-10 | Install Deep Telecom | 24 | 0 | 08-Oct-24 A | 14-Nov-24 A |  | CHI11-MOB-20: FS, CHI-11-MS-02: FS | CHI11-MOB-20, CHI-11-MS-02
CHI11-SU-30 | Install Storm Lines | 30 | 17 | 09-Oct-24 A | 2024-12-06 | 2 | CHI11-SU-10: SS | CHI11-SU-10
CHI11-SU-15 | Install MV Ductbanks | 36 | 6 | 25-Oct-24 A | 2024-11-22 | 2 | CHI11-SU-10: SS | CHI11-SU-10
CHI11-SU-35 | Install Sanitary Lines | 24 | 18 | 04-Nov-24 A | 2024-12-09 | 2 | CHI11-SU-30: SS, CHI11-SU-15: SS | CHI11-SU-30, CHI11-SU-15
CHI11-SU-40 | Install Water Line | 32 | 32 | 04-Nov-24 A | 2024-12-26 | 2 | CHI11-SU-35: SS 10 | CHI11-SU-35
CHI11-SU-50 | Permanent Power (Need by Date) | 0 | 0 | 2025-05-05 |  | 33 | CHI11-03-01-315: SS | CHI11-03-01-315
Under Building Pad |  | 43 | 0 | 08-Oct-24 A | 15-Nov-24 A
CHI11-SU-20 | Install UG Telecom (under Building Pad) | 15 | 0 | 08-Oct-24 A | 10-Oct-24 A |  | CHI11-MOB-10: FF, CHI11-BIM-15: FS, CHI11-MOB-20: SS 4, CHI-11-MS-01: SS, CHI11-SU-10: SS 10 | CHI11-MOB-10, CHI11-BIM-15, CHI11-MOB-20, CHI-11-MS-01, CHI11-SU-10
CHI11-SU-25 | Install UG Electrical / UPM Crossing (under Building Pad) | 25 | 0 | 25-Oct-24 A | 13-Nov-24 A |  | CHI11-SU-20: SS 10 | CHI11-SU-20
CHI11-SU-45 | Backfill after UG work (MV / Telecom) | 2 | 0 | 05-Nov-24 A | 15-Nov-24 A |  | CHI11-SU-25: SS | CHI11-SU-25
Foundations |  | 45 | 0 | 19-Sep-24 A | 12-Nov-24 A
CHI11-FDN-10 | Foundations / Stem Walls (50% Complete) | 25 | 0 | 19-Sep-24 A | 09-Oct-24 A |  | CHI11-MOB-20: FS, CHI11-PROC-10: FS, CHI11-MOB-15: FS 2 | CHI11-MOB-20, CHI11-PROC-10, CHI11-MOB-15
CHI11-FDN-15 | Foundations / Stem Walls (100% Complete) | 20 | 0 | 10-Oct-24 A | 12-Nov-24 A |  | CHI11-FDN-10: FS | CHI11-FDN-10
Core & Shell |  | 92 | 71 | 14-Oct-24 A | 2025-02-14 | 35
Admin/ COLO 3 |  | 70 | 49 | 14-Oct-24 A | 2025-01-17 | 43
CHI11-03-C&S-10 | Admin/C03- Install Primary Steel | 15 | 0 | 14-Oct-24 A | 07-Nov-24 A |  | CHI-11-05-FND-S: SS, CHI11-FDN-10: SS 1, CHI11-RFP-25: FS, CHI11-RFP-30: FS | CHI-11-05-FND-S, CHI11-FDN-10, CHI11-RFP-25, CHI11-RFP-30
CHI11-03-C&S-20 | Admin/C03- UG MEP Work AMS/Gibson | 24 | 23 | 13-Nov-24 A | 2024-12-14 | 0 | CHI11-SU-25: SS 10, CHI11-03-C&S-10: SS, CHI11-03-C&S-15: FF | CHI11-SU-25, CHI11-03-C&S-10, CHI11-03-C&S-15
CHI11-03-C&S-25 | Admin/C03- Install Exterior Wall Panels | 10 | 10 | 18-Nov-24* | 2024-11-29 | 0 | CHI-11-03-PEMB-03: FS, CHI11-03-C&S-10: SS | CHI-11-03-PEMB-03, CHI11-03-C&S-10
CHI11-03-C&S-15 | Admin/C03- Install Roof Panels | 12 | 12 | 2024-11-30 | 2024-12-14 | 0 | CHI11-03-C&S-25: FS, CHI-11-03-PEMB-03: FS, CHI11-03-C&S-10: FS, CHI-11-MS-04: SS | CHI11-03-C&S-25, CHI-11-03-PEMB-03, CHI11-03-C&S-10, CHI-11-MS-04
CHI11-03-C&S-30 | Admin/C03- Install Louvers & Dampers | 16 | 16 | 2024-12-16 | 2025-01-06 | 35 | CHI11-03-C&S-15: FS | CHI11-03-C&S-15
CHI11-03-C&S-35 | Admin/C03- Prep / Place SOG | 10 | 10 | 2024-12-16 | 2024-12-27 | 0 | CHI11-03-C&S-15: FS, CHI11-03-C&S-25: FS, CHI11-03-C&S-20: FS | CHI11-03-C&S-15, CHI11-03-C&S-25, CHI11-03-C&S-20
CHI11-03-C&S-40 | Admin/C03- Install Misc. Metals (Trims, Gutters, Catwalks) | 16 | 16 | 2024-12-30 | 2025-01-17 | 43 | CHI11-03-C&S-35: FS | CHI11-03-C&S-35
CHI11-03-C&S-45 | Admin/C03- Weather Days | 15 | 15 | 2024-12-30 | 2025-01-16 | 0 | CHI11-03-C&S-35: FS | CHI11-03-C&S-35
COLO 4 |  | 70 | 59 | 01-Nov-24 A | 2025-01-30 | 31
CHI11-04-C&S-10 | C04- Install Primary Steel | 15 | 4 | 01-Nov-24 A | 2024-11-20 | 19 | CHI11-FDN-15: FF 6, CHI11-03-C&S-10: SS 10 | CHI11-FDN-15, CHI11-03-C&S-10
CHI11-04-C&S-25 | C04- Install Exterior Wall Panels | 19 | 19 | 2024-11-21 | 2024-12-14 | 19 | CHI-11-MS-04: SS, CHI11-03-C&S-10: FS, CHI11-04-C&S-10: FS | CHI-11-MS-04, CHI11-03-C&S-10, CHI11-04-C&S-10
CHI11-04-C&S-20 | C04- UG MEP Work AMS/Gibson | 19 | 19 | 2024-12-04 | 2024-12-27 | 19 | CHI11-03-C&S-20: SS 15, CHI11-04-C&S-25: SS 10 | CHI11-03-C&S-20, CHI11-04-C&S-25
CHI11-04-C&S-15 | C04- Install Roof Panels | 12 | 12 | 2024-12-16 | 2024-12-31 | 39 | CHI11-04-C&S-25: FS | CHI11-04-C&S-25
CHI11-04-C&S-30 | C04- Prep / Place SOG | 10 | 10 | 2024-12-30 | 2025-01-10 | 19 | CHI11-04-C&S-20: FS, CHI11-SU-45: FS, CHI11-04-C&S-25: FS | CHI11-04-C&S-20, CHI11-SU-45, CHI11-04-C&S-25
CHI11-04-C&S-35 | C04- Install Louvers & Dampers | 16 | 16 | 2025-01-07 | 2025-01-25 | 35 | CHI11-03-C&S-30: FS, CHI11-04-C&S-15: FS | CHI11-03-C&S-30, CHI11-04-C&S-15
CHI11-04-C&S-40 | C04- Install Misc. Metals (Trims, Gutters, Catwalks) | 16 | 16 | 2025-01-11 | 2025-01-30 | 19 | CHI11-04-C&S-30: FS | CHI11-04-C&S-30
COLO 5 |  | 72 | 71 | 12-Nov-24 A | 2025-02-14 | 35
CHI11-05-C&S-10 | C05- Install Primary Steel | 15 | 14 | 12-Nov-24 A | 2024-12-03 | 40 | CHI-11-05-FND-F: FF, CHI11-04-C&S-10: SS 11, CHI-11-MS-03: FS | CHI-11-05-FND-F, CHI11-04-C&S-10, CHI-11-MS-03
CHI11-05-C&S-25 | C05- Install Exterior Wall Panels | 21 | 21 | 2024-12-04 | 2024-12-31 | 40 | CHI-11-MS-05: FS | CHI-11-MS-05
CHI11-05-C&S-20 | C05- UG MEP Work AMS/Gibson | 21 | 21 | 2024-12-17 | 2025-01-13 | 35 | CHI11-04-C&S-20: SS 10, CHI11-05-C&S-25: SS 5 | CHI11-04-C&S-20, CHI11-05-C&S-25
CHI11-05-C&S-15 | C05- Install Roof Panels | 12 | 12 | 2025-01-02 | 2025-01-15 | 43 | CHI11-05-C&S-10: FS, CHI-11-MS-04: SS, CHI11-05-C&S-25: FS | CHI11-05-C&S-10, CHI-11-MS-04, CHI11-05-C&S-25
CHI11-05-C&S-30 | C05- Prep / Place SOG | 10 | 10 | 2025-01-14 | 2025-01-25 | 35 | CHI11-05-C&S-20: FS, CHI11-05-C&S-25: FS | CHI11-05-C&S-20, CHI11-05-C&S-25
CHI11-05-C&S-35 | C05- Install Louvers & Dampers | 16 | 16 | 2025-01-27 | 2025-02-14 | 35 | CHI11-05-C&S-40: FF, CHI11-04-C&S-35: FS, CHI-11-MS-08: FS, CHI11-05-C&S-15: FS | CHI11-05-C&S-40, CHI11-04-C&S-35, CHI-11-MS-08, CHI11-05-C&S-15
CHI11-05-C&S-40 | C05- Install Misc. Metals (Trims, Gutters, Catwalks) | 16 | 16 | 2025-01-27 | 2025-02-14 | 35 | CHI11-05-C&S-30: FS | CHI11-05-C&S-30
Electrical Yard |  | 122 | 122 | 2025-01-17 | 2025-06-18 | 61
Admin/ COLO 3 |  | 110 | 110 | 2025-01-17 | 2025-06-03 | 4
CHI11-03-YARD-10 | C03/Yard- Build Equipment Pads for XFMs | 9 | 9 | 2025-01-17 | 2025-01-28 | 26 | CHI11-03-C&S-45: FS, CHI11-03-C&S-30: FS, CHI11-FDN-10: FS | CHI11-03-C&S-45, CHI11-03-C&S-30, CHI11-FDN-10
CHI11-03-YARD-15 | C03/Yard- Build Equipment Pads for UPMs | 9 | 9 | 2025-01-29 | 2025-02-07 | 26 | CHI11-03-YARD-10: FS | CHI11-03-YARD-10
CHI11-03-YARD-20 | C03/Yard- Build Equipment Pads for UMSs | 9 | 9 | 2025-02-10 | 2025-02-19 | 26 | CHI11-03-YARD-15: FS | CHI11-03-YARD-15
CHI11-03-YARD-25 | C03/Yard- Build Equipment Pads for Generators | 9 | 9 | 2025-02-20 | 2025-03-03 | 26 | CHI11-03-YARD-20: FS | CHI11-03-YARD-20
CHI11-03-YARD-30 | C03/Yard- Install XFMs | 11 | 11 | 2025-03-04 | 2025-03-15 | 38 | CHI-11-03-XFM-03: FS, CHI11-03-YARD-25: FS | CHI-11-03-XFM-03, CHI11-03-YARD-25
CHI11-03-YARD-35 | C03/Yard- Install UPMs | 11 | 11 | 2025-03-04 | 2025-03-15 | 38 | CHI-11-03-UPM-03: FS, CHI11-03-YARD-30: FF | CHI-11-03-UPM-03, CHI11-03-YARD-30
CHI11-03-YARD-40 | C03/Yard- Install UMSs | 11 | 11 | 2025-03-04 | 2025-03-15 | 38 | CHI-11-03-MVS-03: FS, CHI11-RFP-10: FS, CHI11-03-YARD-35: FF | CHI-11-03-MVS-03, CHI11-RFP-10, CHI11-03-YARD-35
CHI11-03-YARD-45 | C03/Yard- Install Generators | 11 | 11 | 2025-03-04 | 2025-03-15 | 38 | CHI-11-03-GEN-03: FS, CHI11-03-YARD-40: FF | CHI-11-03-GEN-03, CHI11-03-YARD-40
CHI11-03-YARD-50 | C03/Yard- MV Cable Pulling & Terminating to Cell 1 | 8 | 8 | 2025-04-25 | 2025-05-05 | 4 | CHI-11-CFCI-25: FS, CHI-11-CFCI-20: FS, CHI11-03-YARD-45: FF 6 | CHI-11-CFCI-25, CHI-11-CFCI-20, CHI11-03-YARD-45
CHI11-03-YARD-55 | C03/Yard- MV Cable Pulling & Terminating to Cell 2 | 8 | 8 | 2025-05-06 | 2025-05-14 | 4 | CHI11-03-YARD-50: FS, CHI11-03-YARD-45: FS | CHI11-03-YARD-50, CHI11-03-YARD-45
CHI11-03-YARD-60 | C03/Yard- MV Cable Pulling & Terminating to Cell 4 | 8 | 8 | 2025-05-15 | 2025-05-23 | 4 | CHI11-03-YARD-55: FS, CHI11-03-YARD-45: FS | CHI11-03-YARD-55, CHI11-03-YARD-45
CHI11-03-YARD-65 | C03/Yard- MV Cable Pulling & Terminating to Cell 3 | 7 | 7 | 2025-05-27 | 2025-06-03 | 4 | CHI11-03-YARD-60: FS, CHI11-03-YARD-45: FS | CHI11-03-YARD-60, CHI11-03-YARD-45
COLO 4 |  | 83 | 83 | 2025-02-21 | 2025-06-04 | 37
CHI11-04-YARD-10 | C04/Yard- Build Equipment Pads for XFMs | 9 | 9 | 2025-02-21 | 2025-03-04 | 26 | CHI11-03-YARD-25: SS 1, CHI11-04-C&S-35: SS 7 | CHI11-03-YARD-25, CHI11-04-C&S-35
CHI11-04-YARD-15 | C04/Yard- Build Equipment Pads for UPMs | 9 | 9 | 2025-03-05 | 2025-03-14 | 26 | CHI11-04-YARD-10: FS | CHI11-04-YARD-10
CHI11-04-YARD-20 | C04/Yard- Build Equipment Pads for UMSs | 9 | 9 | 2025-03-15 | 2025-03-26 | 26 | CHI11-04-YARD-15: FS | CHI11-04-YARD-15
CHI11-04-YARD-25 | C04/Yard- Build Equipment Pads for Generators | 9 | 9 | 2025-03-27 | 2025-04-05 | 26 | CHI11-04-YARD-20: FS | CHI11-04-YARD-20
CHI11-04-YARD-30 | C04/Yard- Install XFMs | 11 | 11 | 2025-04-02 | 2025-04-15 | 34 | CHI-11-04-XFM-03: FS, CHI11-04-YARD-25: SS 5 | CHI-11-04-XFM-03, CHI11-04-YARD-25
CHI11-04-YARD-35 | C04/Yard- Install UPMs | 11 | 11 | 2025-04-02 | 2025-04-15 | 34 | CHI-11-04-UPM-03: FS, CHI11-04-YARD-30: FF | CHI-11-04-UPM-03, CHI11-04-YARD-30
CHI11-04-YARD-40 | C04/Yard- Install UMSs | 11 | 11 | 2025-04-02 | 2025-04-15 | 34 | CHI-11-04-MVS-03: FS, CHI11-04-YARD-35: FF | CHI-11-04-MVS-03, CHI11-04-YARD-35
CHI11-04-YARD-45 | C04/Yard- Install Generators | 11 | 11 | 2025-04-11 | 2025-04-24 | 26 | CHI-11-04-GEN-03: FS, CHI11-04-YARD-40: FF | CHI-11-04-GEN-03, CHI11-04-YARD-40
CHI11-04-YARD-50 | C04/Yard- MV Cable Pulling & Terminating to Cell 1 | 8 | 8 | 2025-04-25 | 2025-05-05 | 26 | CHI-11-CFCI-25: FS, CHI-11-CFCI-20: FS, CHI11-04-YARD-45: FS | CHI-11-CFCI-25, CHI-11-CFCI-20, CHI11-04-YARD-45
CHI11-04-YARD-55 | C04/Yard- MV Cable Pulling & Terminating to Cell 2 | 8 | 8 | 2025-05-06 | 2025-05-14 | 37 | CHI11-04-YARD-50: FS, CHI11-04-YARD-45: FS | CHI11-04-YARD-50, CHI11-04-YARD-45
CHI11-04-YARD-60 | C04/Yard- MV Cable Pulling & Terminating to Cell 4 | 8 | 8 | 2025-05-15 | 2025-05-23 | 37 | CHI11-04-YARD-55: FS, CHI11-04-YARD-45: FS | CHI11-04-YARD-55, CHI11-04-YARD-45
CHI11-04-YARD-65 | C04/Yard- MV Cable Pulling & Terminating to Cell 3 | 8 | 8 | 2025-05-27 | 2025-06-04 | 37 | CHI11-04-YARD-60: FS, CHI11-04-YARD-45: FS | CHI11-04-YARD-60, CHI11-04-YARD-45
COLO 5 |  | 66 | 66 | 2025-03-28 | 2025-06-18 | 61
CHI11-05-YARD-10 | C05/Yard- Build Equipment Pads for XFMs | 9 | 9 | 2025-03-28 | 2025-04-07 | 39 | CHI11-04-YARD-25: SS 1, CHI11-05-C&S-35: SS 7 | CHI11-04-YARD-25, CHI11-05-C&S-35
CHI11-05-YARD-15 | C05/Yard- Build Equipment Pads for UPMs | 9 | 9 | 2025-04-08 | 2025-04-18 | 39 | CHI11-05-YARD-10: FS | CHI11-05-YARD-10
CHI11-05-YARD-20 | C05/Yard- Build Equipment Pads for UMSs | 9 | 9 | 2025-04-19 | 2025-04-29 | 39 | CHI11-05-YARD-15: FS | CHI11-05-YARD-15
CHI11-05-YARD-25 | C05/Yard- Build Equipment Pads for Generators | 9 | 9 | 2025-04-30 | 2025-05-10 | 39 | CHI11-05-YARD-20: FS | CHI11-05-YARD-20
CHI11-05-YARD-30 | C05/Yard- MV Cable Pulling & Terminating(To Junction Box) to Cell 1 | 8 | 8 | 2025-05-02 | 2025-05-12 | 41 | CHI11-05-YARD-25: SS 2 | CHI11-05-YARD-25
CHI11-05-YARD-35 | C05/Yard- Install XFMs | 11 | 11 | 2025-05-12 | 2025-05-23 | 39 | CHI-11-05-XFM-03: FS, CHI11-05-YARD-25: FS | CHI-11-05-XFM-03, CHI11-05-YARD-25
CHI11-05-YARD-40 | C05/Yard- MV Cable Pulling & Terminating(To Junction Box) to Cell 2 | 8 | 8 | 2025-05-13 | 2025-05-21 | 46 | CHI11-05-YARD-30: FS | CHI11-05-YARD-30
CHI11-05-YARD-45 | C05/Yard- Install UPMs | 10 | 10 | 2025-05-14 | 2025-05-27 | 39 | CHI-11-05-UPM-03: FS, CHI11-05-YARD-35: FF 1 | CHI-11-05-UPM-03, CHI11-05-YARD-35
CHI11-05-YARD-50 | C05/Yard- Install UMSs | 10 | 10 | 2025-05-16 | 2025-05-29 | 39 | CHI-11-05-MVS-03: FS, CHI11-05-YARD-45: FF 2 | CHI-11-05-MVS-03, CHI11-05-YARD-45
CHI11-05-YARD-55 | C05/Yard- Install Generators | 10 | 10 | 2025-05-19 | 2025-05-31 | 39 | CHI-11-05-GEN-03: FS, CHI11-05-YARD-50: FF 2 | CHI-11-05-GEN-03, CHI11-05-YARD-50
CHI11-05-YARD-60 | C05/Yard- MV Cable Pulling & Terminating(To Junction Box) to Cell 4 | 7 | 7 | 2025-05-22 | 2025-05-31 | 47 | CHI11-05-YARD-40: FS | CHI11-05-YARD-40
CHI11-05-YARD-65 | C05/Yard- Terminate MV Gear - Cell 1 | 4 | 4 | 2025-05-30 | 2025-06-03 | 44 | CHI-11-CFCI-25: FS, CHI-11-CFCI-20: FS, CHI11-05-YARD-55: FF 2 | CHI-11-CFCI-25, CHI-11-CFCI-20, CHI11-05-YARD-55
CHI11-05-YARD-70 | C05/Yard- MV Cable Pulling & Terminating(To Junction Box) to Cell 3 | 8 | 8 | 2025-06-02 | 2025-06-10 | 47 | CHI11-05-YARD-60: FS | CHI11-05-YARD-60
CHI11-05-YARD-75 | C05/Yard- Terminate MV Gear - Cell 2 | 4 | 4 | 2025-06-04 | 2025-06-07 | 53 | CHI11-05-YARD-65: FS | CHI11-05-YARD-65
CHI11-05-YARD-80 | C05/Yard- Terminate MV Gear - Cell 4 | 4 | 4 | 2025-06-09 | 2025-06-12 | 57 | CHI11-05-YARD-75: FS | CHI11-05-YARD-75
CHI11-05-YARD-85 | C05/Yard- Terminate MV Gear - Cell 3 | 4 | 4 | 2025-06-13 | 2025-06-18 | 61 | CHI11-05-YARD-80: FS | CHI11-05-YARD-80
Fitout |  | 173 | 173 | 2025-01-17 | 2025-08-21 | 5
Admin Area |  | 90 | 90 | 2025-01-20 | 2025-05-09 | 43
Beneficial Use Rooms |  | 90 | 90 | 2025-01-20 | 2025-05-09 | 43
Electrical Room |  | 72 | 72 | 2025-01-20 | 2025-04-17 | 57
CHI11-ADMIN-10 | Admin/Elec Rm- Fire Protection OH R/I | 1 | 1 | 2025-01-20 | 2025-01-20 | 43 | CHI11-03-01-10: FS, CHI-11-03-DRY-F: FS, CHI11-SU-40: FS, CHI11-03-C&S-40: FS | CHI11-03-01-10, CHI-11-03-DRY-F, CHI11-SU-40, CHI11-03-C&S-40
CHI11-ADMIN-15 | Admin/ Elec Rm- Framing | 1 | 1 | 2025-01-21 | 2025-01-21 | 43 | CHI11-ADMIN-10: FS, CHI11-03-C&S-40: FS | CHI11-ADMIN-10, CHI11-03-C&S-40
CHI11-ADMIN-25 | Admin/ Elec Rm- MEP Rough-In & OH | 2 | 2 | 2025-01-22 | 2025-01-23 | 43 | CHI11-ADMIN-15: FS | CHI11-ADMIN-15
CHI11-ADMIN-50 | Admin/ Elec Rm- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-01-24 | 2025-01-25 | 78 | CHI11-ADMIN-25: FS | CHI11-ADMIN-25
CHI11-ADMIN-80 | Admin/ Elec Rm- Secondary / Ceiling Steel | 1 | 1 | 2025-01-27 | 2025-01-27 | 78 | CHI11-ADMIN-50: FS | CHI11-ADMIN-50
CHI11-ADMIN-105 | Admin/ Elec Rm- Finsh Drywall and Wall Protection | 4 | 4 | 2025-01-28 | 2025-01-31 | 78 | CHI11-ADMIN-80: FS | CHI11-ADMIN-80
CHI11-ADMIN-200 | Admin/ Elec Rm- Paint | 2 | 2 | 2025-02-01 | 2025-02-03 | 78 | CHI11-ADMIN-105: FS | CHI11-ADMIN-105
CHI11-ADMIN-220 | Admin/ Elec Rm- Cable Tray / Ceiling Steel Height | 1 | 1 | 2025-02-04 | 2025-02-04 | 115 | CHI11-ADMIN-200: FS | CHI11-ADMIN-200
CHI11-ADMIN-230 | Admin/ Elec Rm- Set Electrical Equipment in Admin | 8 | 8 | 2025-03-03 | 2025-03-11 | 57 | CHI-11-04-LVS-03: FS, CHI11-ADMIN-200: FS | CHI-11-04-LVS-03, CHI11-ADMIN-200
CHI11-ADMIN-355 | Admin/ Elec Rm- Pull Feeders to Admin | 14 | 14 | 2025-03-12 | 2025-03-28 | 57 | CHI11-ADMIN-230: FS | CHI11-ADMIN-230
CHI11-ADMIN-435 | Admin/ Elec Rm- Pull Branches From Admin | 12 | 12 | 2025-03-29 | 2025-04-11 | 57 | CHI11-ADMIN-355: FS | CHI11-ADMIN-355
CHI11-ADMIN-460 | Admin/ Elec Rm- Terminate Electrical / Mechanical Equipment | 4 | 4 | 2025-04-14 | 2025-04-17 | 57 | CHI11-ADMIN-220: FF, CHI11-ADMIN-435: FS | CHI11-ADMIN-220, CHI11-ADMIN-435
Entry Room 1 |  | 21 | 21 | 2025-01-21 | 2025-02-14 | 107
CHI11-ADMIN-20 | Admin/ Ent Rm-01- Fire Protection OH R/I | 1 | 1 | 2025-01-21 | 2025-01-21 | 44 | CHI11-ADMIN-10: FS | CHI11-ADMIN-10
CHI11-ADMIN-30 | Admin/ Ent Rm-01- Framing | 1 | 1 | 2025-01-22 | 2025-01-22 | 44 | CHI11-ADMIN-20: FS | CHI11-ADMIN-20
CHI11-ADMIN-55 | Admin/ Ent Rm-01- MEP Rough-In & OH | 2 | 2 | 2025-01-24 | 2025-01-25 | 43 | CHI11-ADMIN-25: FS, CHI11-ADMIN-30: FS | CHI11-ADMIN-25, CHI11-ADMIN-30
CHI11-ADMIN-85 | Admin/ Ent Rm-01- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-01-27 | 2025-01-28 | 107 | CHI11-ADMIN-55: FS | CHI11-ADMIN-55
CHI11-ADMIN-120 | Admin/ Ent Rm-01- Secondary / Ceiling Steel | 1 | 1 | 2025-01-29 | 2025-01-29 | 107 | CHI11-ADMIN-85: FS | CHI11-ADMIN-85
CHI11-ADMIN-155 | Admin/ Ent Rm-01- Finsh Drywall and Wall Protection | 4 | 4 | 2025-01-30 | 2025-02-03 | 107 | CHI11-ADMIN-120: FS | CHI11-ADMIN-120
CHI11-ADMIN-235 | Admin/ Ent Rm-01- Paint | 2 | 2 | 2025-02-04 | 2025-02-05 | 107 | CHI11-ADMIN-155: FS | CHI11-ADMIN-155
CHI11-ADMIN-260 | Admin/ Ent Rm-01- Install Raceway | 3 | 3 | 2025-02-06 | 2025-02-10 | 107 | CHI11-ADMIN-235: FS | CHI11-ADMIN-235
CHI11-ADMIN-310 | Admin/ Ent Rm-01- Set ER-1 Equipment | 4 | 4 | 2025-02-11 | 2025-02-14 | 107 | CHI11-ADMIN-260: FS | CHI11-ADMIN-260
Entry Room 2 |  | 22 | 22 | 2025-01-22 | 2025-02-17 | 105
CHI11-ADMIN-35 | Admin/ Ent Rm-02- Fire Protection OH R/I | 1 | 1 | 2025-01-22 | 2025-01-22 | 45 | CHI11-ADMIN-20: FS | CHI11-ADMIN-20
CHI11-ADMIN-40 | Admin/ Ent Rm-02- Framing | 1 | 1 | 2025-01-23 | 2025-01-23 | 45 | CHI11-ADMIN-35: FS | CHI11-ADMIN-35
CHI11-ADMIN-90 | Admin/ Ent Rm-02- MEP Rough-In & OH | 2 | 2 | 2025-01-27 | 2025-01-28 | 43 | CHI11-ADMIN-55: FS, CHI11-ADMIN-40: FS | CHI11-ADMIN-55, CHI11-ADMIN-40
CHI11-ADMIN-125 | Admin/ Ent Rm-02- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-01-29 | 2025-01-30 | 105 | CHI11-ADMIN-90: FS | CHI11-ADMIN-90
CHI11-ADMIN-170 | Admin/ Ent Rm-02- Secondary / Ceiling Steel | 1 | 1 | 2025-01-31 | 2025-01-31 | 105 | CHI11-ADMIN-125: FS | CHI11-ADMIN-125
CHI11-ADMIN-195 | Admin/ Ent Rm-02- Finsh Drywall and Wall Protection | 4 | 4 | 2025-02-01 | 2025-02-05 | 105 | CHI11-ADMIN-170: FS | CHI11-ADMIN-170
CHI11-ADMIN-265 | Admin/ Ent Rm-02- Paint | 2 | 2 | 2025-02-06 | 2025-02-07 | 105 | CHI11-ADMIN-195: FS | CHI11-ADMIN-195
CHI11-ADMIN-285 | Admin/ Ent Rm-02- Install Raceway | 3 | 3 | 2025-02-10 | 2025-02-12 | 105 | CHI11-ADMIN-265: FS | CHI11-ADMIN-265
CHI11-ADMIN-345 | Admin/ Ent Rm-02- Set ER-2 Equipment | 4 | 4 | 2025-02-13 | 2025-02-17 | 105 | CHI11-ADMIN-285: FS | CHI11-ADMIN-285
FCR (Facilities Control Room) |  | 83 | 83 | 2025-01-23 | 2025-05-05 | 43
CHI11-ADMIN-45 | ADMIN/ FCR- Fire Protection OH R/I | 1 | 1 | 2025-01-23 | 2025-01-23 | 46 | CHI11-ADMIN-35: FS | CHI11-ADMIN-35
CHI11-ADMIN-60 | ADMIN/ FCR- Framing | 1 | 1 | 2025-01-24 | 2025-01-24 | 46 | CHI11-ADMIN-45: FS | CHI11-ADMIN-45
CHI11-ADMIN-130 | ADMIN/ FCR- MEP Rough-In & OH | 2 | 2 | 2025-01-29 | 2025-01-30 | 43 | CHI11-ADMIN-90: FS, CHI11-ADMIN-60: FS | CHI11-ADMIN-90, CHI11-ADMIN-60
CHI11-ADMIN-175 | ADMIN/ FCR- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-01-31 | 2025-02-01 | 43 | CHI11-ADMIN-130: FS | CHI11-ADMIN-130
CHI11-ADMIN-205 | ADMIN/ FCR- Secondary / Ceiling Steel | 1 | 1 | 2025-02-03 | 2025-02-03 | 43 | CHI11-ADMIN-175: FS | CHI11-ADMIN-175
CHI11-ADMIN-225 | ADMIN/ FCR- Finsh Drywall and Wall Protection | 4 | 4 | 2025-02-04 | 2025-02-07 | 43 | CHI11-ADMIN-205: FS | CHI11-ADMIN-205
CHI11-ADMIN-290 | ADMIN/ FCR- Paint | 2 | 2 | 2025-02-10 | 2025-02-11 | 43 | CHI11-ADMIN-225: FS | CHI11-ADMIN-225
CHI11-ADMIN-325 | ADMIN/ FCR- Install Raceway | 3 | 3 | 2025-02-12 | 2025-02-14 | 43 | CHI11-ADMIN-290: FS | CHI11-ADMIN-290
CHI11-ADMIN-375 | ADMIN/ FCR- Set FCR Equipment | 4 | 4 | 2025-02-15 | 2025-02-19 | 43 | CHI11-ADMIN-325: FS | CHI11-ADMIN-325
CHI11-ADMIN-395 | ADMIN/ FCR- Pull Fiber For EPMS VLAN | 12 | 12 | 2025-02-20 | 2025-03-06 | 43 | CHI11-ADMIN-375: FS | CHI11-ADMIN-375
CHI11-ADMIN-400 | ADMIN/ FCR- Pull Copper for EPMS VLAN | 12 | 12 | 2025-02-20 | 2025-03-06 | 43 | CHI11-ADMIN-375: FS | CHI11-ADMIN-375
CHI11-ADMIN-445 | ADMIN/ FCR- Pull Fiber For Tahuya VLAN | 12 | 12 | 2025-03-07 | 2025-03-20 | 43 | CHI11-ADMIN-395: FS | CHI11-ADMIN-395
CHI11-ADMIN-450 | ADMIN/ FCR- Pull Copper for Tahuya VLAN | 12 | 12 | 2025-03-07 | 2025-03-20 | 43 | CHI11-ADMIN-400: FS | CHI11-ADMIN-400
CHI11-ADMIN-465 | ADMIN/ FCR- Pull Fiber For BAS VLAN | 12 | 12 | 2025-03-21 | 2025-04-04 | 43 | CHI11-ADMIN-445: FS | CHI11-ADMIN-445
CHI11-ADMIN-470 | ADMIN/ FCR- Pull Copper for BAS VLAN | 12 | 12 | 2025-03-21 | 2025-04-04 | 43 | CHI11-ADMIN-450: FS | CHI11-ADMIN-450
CHI11-ADMIN-475 | ADMIN/ FCR- Pull Fiber/Copper For CORPNET Network | 12 | 12 | 2025-04-05 | 2025-04-19 | 43 | CHI11-ADMIN-465: FS, CHI11-ADMIN-470: FS | CHI11-ADMIN-465, CHI11-ADMIN-470
CHI11-ADMIN-480 | ADMIN/ FCR- Pull Fiber For CEI Network | 12 | 12 | 2025-04-21 | 2025-05-05 | 43 | CHI11-ADMIN-475: FS | CHI11-ADMIN-475
SER (Security Equipment Room) |  | 22 | 22 | 2025-01-24 | 2025-02-19 | 103
CHI11-ADMIN-65 | ADMIN/ SER- Fire Protection OH R/I | 1 | 1 | 2025-01-24 | 2025-01-24 | 53 | CHI11-ADMIN-45: FS | CHI11-ADMIN-45
CHI11-ADMIN-70 | ADMIN/ SER- Framing | 1 | 1 | 2025-01-25 | 2025-01-25 | 55 | CHI11-ADMIN-65: FS | CHI11-ADMIN-65
CHI11-ADMIN-180 | ADMIN/ SER- MEP Rough-In & OH | 2 | 2 | 2025-01-31 | 2025-02-01 | 51 | CHI11-ADMIN-130: FS, CHI11-ADMIN-70: FS | CHI11-ADMIN-130, CHI11-ADMIN-70
CHI11-ADMIN-210 | ADMIN/ SER- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-02-03 | 2025-02-04 | 103 | CHI11-ADMIN-180: FS | CHI11-ADMIN-180
CHI11-ADMIN-240 | ADMIN/ SER- Secondary / Ceiling Steel | 1 | 1 | 2025-02-05 | 2025-02-05 | 103 | CHI11-ADMIN-210: FS | CHI11-ADMIN-210
CHI11-ADMIN-255 | ADMIN/ SER- Finsh Drywall | 2 | 2 | 2025-02-06 | 2025-02-07 | 103 | CHI11-ADMIN-240: FS | CHI11-ADMIN-240
CHI11-ADMIN-295 | ADMIN/ SER- Paint | 2 | 2 | 2025-02-10 | 2025-02-11 | 103 | CHI11-ADMIN-255: FS | CHI11-ADMIN-255
CHI11-ADMIN-330 | ADMIN/ SER- Install Raceway | 3 | 3 | 2025-02-12 | 2025-02-14 | 103 | CHI11-ADMIN-295: FS | CHI11-ADMIN-295
CHI11-ADMIN-370 | ADMIN/ SER- Set SER Room Equipment | 4 | 4 | 2025-02-15 | 2025-02-19 | 103 | CHI11-ADMIN-330: FS | CHI11-ADMIN-330
STORAGE (High Value & Secure) Rooms |  | 42 | 42 | 2025-01-25 | 2025-03-17 | 82
CHI11-ADMIN-75 | Admin/ High Value Rm- Fire Protection OH R/I | 1 | 1 | 2025-01-25 | 2025-01-25 | 53 | CHI11-ADMIN-65: FS | CHI11-ADMIN-65
CHI11-ADMIN-95 | Admin/ High Value Rm- Framing | 1 | 1 | 2025-01-27 | 2025-01-27 | 56 | CHI11-ADMIN-75: FS | CHI11-ADMIN-75
CHI11-ADMIN-215 | Admin/ High Value Rm- MEP Rough-In & OH | 2 | 2 | 2025-02-03 | 2025-02-04 | 51 | CHI11-ADMIN-180: FS, CHI11-ADMIN-95: FS | CHI11-ADMIN-180, CHI11-ADMIN-95
CHI11-ADMIN-245 | Admin/ High Value Rm- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-02-05 | 2025-02-06 | 82 | CHI11-ADMIN-215: FS | CHI11-ADMIN-215
CHI11-ADMIN-270 | Admin/ High Value Rm- Install Ductwork and Cracs | 15 | 15 | 2025-02-07 | 2025-02-25 | 82 | CHI11-ADMIN-245: FS | CHI11-ADMIN-245
CHI11-ADMIN-420 | Admin/ High Value Rm- Finsh Drywall | 4 | 4 | 2025-02-26 | 2025-03-03 | 82 | CHI11-ADMIN-270: FS | CHI11-ADMIN-270
CHI11-ADMIN-430 | Admin/ High Value Rm- Paint | 2 | 2 | 2025-03-04 | 2025-03-05 | 82 | CHI11-ADMIN-420: FS | CHI11-ADMIN-420
CHI11-ADMIN-440 | Admin/ High Value Rm- Fit-out | 10 | 10 | 2025-03-06 | 2025-03-17 | 82 | CHI11-ADMIN-430: FS | CHI11-ADMIN-430
Punchlist |  | 4 | 4 | 2025-05-06 | 2025-05-09 | 43
CHI11-ADMIN-485 | Admin - Beneficial Rooms PunchList | 4 | 4 | 2025-05-06 | 2025-05-09 | 43 | CHI11-ADMIN-460: FS, CHI11-ADMIN-310: FS, CHI11-ADMIN-345: FS, CHI11-ADMIN-480: FS, CHI11-ADMIN-370: FS, CHI11-ADMIN-440: FS | CHI11-ADMIN-460, CHI11-ADMIN-310, CHI11-ADMIN-345, CHI11-ADMIN-480, CHI11-ADMIN-370, CHI11-ADMIN-440
Remaining Rooms |  | 41 | 41 | 2025-01-27 | 2025-03-17 | 51
Fire Riser Room |  | 24 | 24 | 2025-01-27 | 2025-02-24 | 53
CHI11-ADMIN-100 | Admin/ Fire Riser Rm- Fire Protection OH R/I | 1 | 1 | 2025-01-27 | 2025-01-27 | 53 | CHI11-ADMIN-75: FS | CHI11-ADMIN-75
CHI11-ADMIN-110 | Admin/ Fire Riser Rm- Framing | 1 | 1 | 2025-01-28 | 2025-01-28 | 57 | CHI11-ADMIN-100: FS | CHI11-ADMIN-100
CHI11-ADMIN-145 | Admin/ Fire Riser Rm- Install Duct Work | 2 | 2 | 2025-01-29 | 2025-01-30 | 62 | CHI11-ADMIN-110: FS, CHI11-ADMIN-100: FS | CHI11-ADMIN-110, CHI11-ADMIN-100
CHI11-ADMIN-190 | Admin/ Fire Riser Rm- Install downcomers | 1 | 1 | 2025-01-31 | 2025-01-31 | 62 | CHI11-ADMIN-145: FS | CHI11-ADMIN-145
CHI11-ADMIN-250 | Admin/ Fire Riser Rm- MEP Rough-In & OH | 2 | 2 | 2025-02-05 | 2025-02-06 | 51 | CHI11-ADMIN-215: FS, CHI11-ADMIN-110: FS | CHI11-ADMIN-215, CHI11-ADMIN-110
CHI11-ADMIN-275 | Admin/ Fire Riser Rm- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-02-07 | 2025-02-10 | 54 | CHI11-ADMIN-250: FS | CHI11-ADMIN-250
CHI11-ADMIN-300 | Admin/ Fire Riser Rm- Secondary / Ceiling Steel | 1 | 1 | 2025-02-11 | 2025-02-11 | 54 | CHI11-ADMIN-275: FS | CHI11-ADMIN-275
CHI11-ADMIN-320 | Admin/ Fire Riser Rm- Finsh Drywall | 2 | 2 | 2025-02-12 | 2025-02-13 | 54 | CHI11-ADMIN-190: FS, CHI11-ADMIN-300: FS | CHI11-ADMIN-190, CHI11-ADMIN-300
CHI11-ADMIN-350 | Admin/ Fire Riser Rm- Paint | 2 | 2 | 2025-02-14 | 2025-02-15 | 54 | CHI11-ADMIN-320: FS | CHI11-ADMIN-320
CHI11-ADMIN-380 | Admin/ Fire Riser Rm- Ceiling Grid & Tile | 4 | 4 | 2025-02-18 | 2025-02-21 | 53 | CHI11-ADMIN-160: FS, CHI11-ADMIN-350: FS | CHI11-ADMIN-160, CHI11-ADMIN-350
CHI11-ADMIN-415 | Admin/ Fire Riser Rm- Complete Pipe/ Valves | 2 | 2 | 2025-02-22 | 2025-02-24 | 53 | CHI11-ADMIN-380: FS | CHI11-ADMIN-380
Restrooms & Janitor Room |  | 21 | 21 | 2025-01-28 | 2025-02-21 | 51
CHI11-ADMIN-115 | Admin/ Other- Fire Protection OH R/I | 1 | 1 | 2025-01-28 | 2025-01-28 | 53 | CHI11-ADMIN-100: FS | CHI11-ADMIN-100
CHI11-ADMIN-135 | Admin/ Other- Framing | 1 | 1 | 2025-01-29 | 2025-01-29 | 58 | CHI11-ADMIN-115: FS | CHI11-ADMIN-115
CHI11-ADMIN-280 | Admin/ Other- MEP Rough-In & OH | 2 | 2 | 2025-02-07 | 2025-02-10 | 51 | CHI11-ADMIN-250: FS, CHI11-ADMIN-135: FS | CHI11-ADMIN-250, CHI11-ADMIN-135
CHI11-ADMIN-305 | Admin/ Other- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-02-11 | 2025-02-12 | 51 | CHI11-ADMIN-280: FS | CHI11-ADMIN-280
CHI11-ADMIN-335 | Admin/ Other- Finsh Drywall | 2 | 2 | 2025-02-13 | 2025-02-14 | 51 | CHI11-ADMIN-305: FS | CHI11-ADMIN-305
CHI11-ADMIN-360 | Admin/ Other- Paint | 2 | 2 | 2025-02-15 | 2025-02-17 | 51 | CHI11-ADMIN-335: FS | CHI11-ADMIN-335
CHI11-ADMIN-385 | Admin/ Other- Ceiling Grid & Tile | 4 | 4 | 2025-02-18 | 2025-02-21 | 51 | CHI11-ADMIN-360: FS | CHI11-ADMIN-360
Loading Dock |  | 36 | 36 | 2025-01-29 | 2025-03-13 | 54
CHI11-ADMIN-140 | Admin/ Loading Dock- Fire Protection OH R/I | 1 | 1 | 2025-01-29 | 2025-01-29 | 53 | CHI11-ADMIN-115: FS | CHI11-ADMIN-115
CHI11-ADMIN-150 | Admin/ Loading Dock- Install Ductwork | 15 | 15 | 2025-01-29 | 2025-02-15 | 55 | CHI11-ADMIN-140: SS | CHI11-ADMIN-140
CHI11-ADMIN-160 | Admin/ Loading Dock- Install Ductwork (Remaining Rooms, Corridor) | 15 | 15 | 2025-01-30 | 2025-02-17 | 53 | CHI11-ADMIN-140: FS, CHI11-ADMIN-100: FS | CHI11-ADMIN-140, CHI11-ADMIN-100
CHI11-ADMIN-165 | Admin/ Loading Dock- Framing | 1 | 1 | 2025-01-30 | 2025-01-30 | 62 | CHI11-ADMIN-140: FS | CHI11-ADMIN-140
CHI11-ADMIN-185 | Admin/ Loading Dock- Rough-in | 1 | 1 | 2025-01-31 | 2025-01-31 | 84 | CHI11-ADMIN-165: FS | CHI11-ADMIN-165
CHI11-ADMIN-315 | Admin/ Loading Dock- MEP Rough-In & OH | 2 | 2 | 2025-02-11 | 2025-02-12 | 54 | CHI11-ADMIN-280: FF, CHI11-ADMIN-280: FS, CHI11-ADMIN-165: FS | CHI11-ADMIN-280, CHI11-ADMIN-280, CHI11-ADMIN-165
CHI11-ADMIN-340 | Admin/ Loading Dock- Top Out Drywall - Ceiling Steel Height | 2 | 2 | 2025-02-13 | 2025-02-14 | 54 | CHI11-ADMIN-315: FS | CHI11-ADMIN-315
CHI11-ADMIN-365 | Admin/ Loading Dock- Finsh Drywall | 2 | 2 | 2025-02-15 | 2025-02-17 | 54 | CHI11-ADMIN-340: FS | CHI11-ADMIN-340
CHI11-ADMIN-390 | Admin/ Loading Dock- Paint | 2 | 2 | 2025-02-18 | 2025-02-19 | 54 | CHI11-ADMIN-150: FS, CHI11-ADMIN-365: FS | CHI11-ADMIN-150, CHI11-ADMIN-365
CHI11-ADMIN-405 | Admin/ Loading Dock- Plumbing | 15 | 15 | 2025-02-20 | 2025-03-10 | 54 | CHI11-ADMIN-390: FS | CHI11-ADMIN-390
CHI11-ADMIN-455 | Admin/ Loading Dock- Pull Cables | 3 | 3 | 2025-03-11 | 2025-03-13 | 54 | CHI11-ADMIN-405: FS, CHI11-ADMIN-185: FS | CHI11-ADMIN-405, CHI11-ADMIN-185
Admin Gen Finishes & Punch |  | 19 | 19 | 2025-02-22 | 2025-03-17 | 51
CHI11-ADMIN-410 | ADMIN- Install Doors | 4 | 4 | 2025-02-22 | 2025-02-26 | 51 | CHI11-ADMIN-385: FS | CHI11-ADMIN-385
CHI11-ADMIN-425 | ADMIN- Light Fixtures Installation | 10 | 10 | 2025-02-27 | 2025-03-11 | 51 | CHI11-ADMIN-415: FS, CHI11-ADMIN-380: FS, CHI11-ADMIN-410: FS | CHI11-ADMIN-415, CHI11-ADMIN-380, CHI11-ADMIN-410
CHI11-ADMIN-490 | ADMIN- Remaining Area Punchlist | 5 | 5 | 2025-03-12 | 2025-03-17 | 51 | CHI11-ADMIN-425: FS | CHI11-ADMIN-425
COLO 3 |  | 124 | 124 | 2025-01-17 | 2025-06-20 | 0
COLO 3 - CELL 1 |  | 82 | 82 | 2025-01-17 | 2025-04-28 | 17
COLO 3 - CELL 1 Data Hall |  | 72 | 72 | 2025-01-17 | 2025-04-16 | 17
CHI11-03-01-10 | C03/01-DH- Layout Framing | 1 | 1 | 2025-01-17 | 2025-01-17 | 0 | CHI11-03-C&S-45: FS, CHI11-03-C&S-35: FS, CHI-11-03-DRY-F: FS | CHI11-03-C&S-45, CHI11-03-C&S-35, CHI-11-03-DRY-F
CHI11-03-01-15 | C03/01-DH- Install Framing | 5 | 5 | 2025-01-20 | 2025-01-24 | 0 | CHI11-03-01-10: FS | CHI11-03-01-10
CHI11-03-01-20 | C03/01-DH- In-Wall R/I | 3 | 3 | 2025-01-25 | 2025-01-28 | 0 | CHI11-03-01-15: FS | CHI11-03-01-15
CHI11-03-01-30 | C03/01-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-01-29 | 2025-01-31 | 14 | CHI11-03-01-20: FS | CHI11-03-01-20
CHI11-03-01-35 | C03/01-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-01-29 | 2025-01-31 | 0 | CHI11-03-01-20: FS | CHI11-03-01-20
CHI11-03-01-45 | C03/01-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-02-01 | 2025-02-04 | 14 | CHI11-03-01-30: FS | CHI11-03-01-30
CHI11-03-01-50 | C03/01-DH- Overhead R/I - Electrical | 4 | 4 | 2025-02-01 | 2025-02-05 | 14 | CHI11-03-01-45: SS | CHI11-03-01-45
CHI11-03-01-55 | C03/01-DH- Finish Dry-Wall | 3 | 3 | 2025-02-01 | 2025-02-04 | 11 | CHI11-03-01-35: FS | CHI11-03-01-35
CHI11-03-01-60 | C03/01-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-02-04 | 2025-02-05 | 14 | CHI11-03-01-50: FF | CHI11-03-01-50
CHI11-03-01-70 | C03/01-DH- Paint Dry-Wall | 3 | 3 | 2025-02-05 | 2025-02-07 | 11 | CHI11-03-01-55: FS | CHI11-03-01-55
CHI11-03-01-65 | C03/01-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-02-06 | 2025-02-07 | 14 | CHI11-03-01-60: FS, CHI11-03-01-50: FS | CHI11-03-01-60, CHI11-03-01-50
CHI11-03-01-75 | C03/01-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-02-10 | 2025-02-12 | 11 | CHI11-03-01-70: FS | CHI11-03-01-70
CHI11-03-01-90 | C03/01-DH- Install Secondary Steel | 2 | 2 | 2025-02-13 | 2025-02-14 | 11 | CHI11-03-01-65: FS, CHI11-03-01-75: FS | CHI11-03-01-65, CHI11-03-01-75
CHI11-03-01-110 | C03/01-DH- Paint Secondary Steel | 2 | 2 | 2025-02-15 | 2025-02-17 | 11 | CHI11-03-01-90: FS | CHI11-03-01-90
CHI11-03-01-135 | C03/01-DH- General Cleaning | 1 | 1 | 2025-02-18 | 2025-02-18 | 11 | CHI11-03-01-110: FS | CHI11-03-01-110
CHI11-03-01-140 | C03/01-DH- Install Ceiling Grid | 4 | 4 | 2025-02-18 | 2025-02-21 | 33 | CHI11-03-01-60: FS, CHI11-03-01-65: FS, CHI11-03-01-110: FS | CHI11-03-01-60, CHI11-03-01-65, CHI11-03-01-110
CHI11-03-01-150 | C03/01-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-02-22 | 2025-02-26 | 36 | CHI11-03-01-140: FS | CHI11-03-01-140
CHI11-03-01-155 | C03/01-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-02-22 | 2025-02-27 | 33 | CHI-11-03-HAC-03: FS, CHI-11-CFCI-30: FS, CHI11-03-01-140: FS, CHI11-03-01-135: FS | CHI-11-03-HAC-03, CHI-11-CFCI-30, CHI11-03-01-140, CHI11-03-01-135
CHI11-03-01-165 | C03/01-DH- Install Busways on HAC Arms | 5 | 5 | 2025-02-25 | 2025-03-03 | 33 | CHI-11-03-BUS-03: FS, CHI11-03-01-155: FF 2 | CHI-11-03-BUS-03, CHI11-03-01-155
CHI11-03-01-175 | C03/01-DH- Install Device Tiles | 2 | 2 | 2025-02-27 | 2025-02-28 | 36 | CHI11-03-01-150: FS | CHI11-03-01-150
CHI11-03-01-180 | C03/01-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-02-27 | 2025-03-05 | 33 | CHI11-03-01-165: FF 2 | CHI11-03-01-165
CHI11-03-01-185 | C03/01-DH- Set PDUs | 4 | 4 | 2025-02-27 | 2025-03-04 | 41 | CHI-11-03-PDU-03: FS, CHI11-03-01-150: FS | CHI-11-03-PDU-03, CHI11-03-01-150
CHI11-03-01-200 | C03/01-DH- Raise HACs | 4 | 4 | 2025-03-06 | 2025-03-10 | 33 | CHI11-03-01-175: FS, CHI11-03-01-180: FS | CHI11-03-01-175, CHI11-03-01-180
CHI11-03-01-235 | C03/01-DH- Detail HACs | 4 | 4 | 2025-03-11 | 2025-03-14 | 43 | CHI11-03-01-200: FS | CHI11-03-01-200
CHI11-03-01-240 | C03/01-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-03-11 | 2025-03-13 | 33 | CHI11-03-01-200: FS | CHI11-03-01-200
CHI11-03-01-260 | C03/01-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-03-14 | 2025-03-17 | 33 | CHI11-03-01-185: FS, CHI11-03-01-240: FS | CHI11-03-01-185, CHI11-03-01-240
CHI11-03-01-275 | C03/01-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-03-18 | 2025-03-24 | 33 | CHI11-03-01-260: FS | CHI11-03-01-260
CHI11-03-01-305 | C03/01-DH- Terminate PDUs | 3 | 3 | 2025-04-14 | 2025-04-16 | 17 | CHI11-03-01-275: FS, CHI11-03-01-295: FS | CHI11-03-01-275, CHI11-03-01-295
COLO 3 - CELL 1 Electrical Room |  | 63 | 63 | 2025-01-25 | 2025-04-11 | 0
CHI11-03-01-25 | C03/01-Elec Rm- Install Framing | 5 | 5 | 2025-01-25 | 2025-01-30 | 1 | CHI11-03-01-15: FS | CHI11-03-01-15
CHI11-03-01-40 | C03/01-Elec Rm- In-Wall R/I | 8 | 8 | 2025-01-31 | 2025-02-10 | 1 | CHI11-03-01-25: FS | CHI11-03-01-25
CHI11-03-01-80 | C03/01-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-02-11 | 2025-02-12 | 15 | CHI11-03-01-40: FS | CHI11-03-01-40
CHI11-03-01-85 | C03/01-Elec Rm- Install Drywall [Elec + Battery Rooms] | 10 | 10 | 2025-02-11 | 2025-02-21 | 1 | CHI11-03-01-40: FS | CHI11-03-01-40
CHI11-03-01-95 | C03/01-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-02-13 | 2025-02-14 | 15 | CHI11-03-01-80: FS | CHI11-03-01-80
CHI11-03-01-100 | C03/01-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-02-13 | 2025-02-15 | 15 | CHI11-03-01-95: SS | CHI11-03-01-95
CHI11-03-01-115 | C03/01-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-02-15 | 2025-02-15 | 15 | CHI11-03-01-100: FF | CHI11-03-01-100
CHI11-03-01-130 | C03/01-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-02-17 | 2025-02-18 | 15 | CHI11-03-01-115: FS | CHI11-03-01-115
CHI11-03-01-160 | C03/01-Elec Rm- Finish Dry-Wall | 8 | 8 | 2025-02-22 | 2025-03-04 | 1 | CHI11-03-01-85: FS | CHI11-03-01-85
CHI11-03-01-195 | C03/01-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-03-05 | 2025-03-06 | 1 | CHI11-03-01-160: FS | CHI11-03-01-160
CHI11-03-01-215 | C03/01-Elec Rm- General Cleaning | 1 | 1 | 2025-03-07 | 2025-03-07 | 1 | CHI11-03-01-195: FS | CHI11-03-01-195
CHI11-03-01-230 | C03/01-Elec Rm- Set Electrical Equipments | 6 | 6 | 2025-03-10 | 2025-03-15 | 0 | CHI-11-03-TCP-01: SS, CHI-11-03-MSB-03: FS, CHI-11-03-ADP-03: FS, CHI-11-03-TCP-03: FS, CHI-11-03-UPS-03: FS, CHI-11-03-LVS-03: FS, CHI-11-03-HAC-03: FS, CHI-11-03-EPMS-03: FS, CHI-11-03-ATS-03: FS, CHI-11-03-ROJ-F: FF, CHI11-03-01-215: FS, CHI11-03-01-130: FS | CHI-11-03-TCP-01, CHI-11-03-MSB-03, CHI-11-03-ADP-03, CHI-11-03-TCP-03, CHI-11-03-UPS-03, CHI-11-03-LVS-03, CHI-11-03-HAC-03, CHI-11-03-EPMS-03, CHI-11-03-ATS-03, CHI-11-03-ROJ-F, CHI11-03-01-215, CHI11-03-01-130
CHI11-03-01-270 | C03/01-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | 11 | 11 | 2025-03-17 | 2025-03-29 | 0 | CHI11-03-01-230: FS | CHI11-03-01-230
CHI11-03-01-290 | C03/01-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-03-31 | 2025-04-03 | 0 | CHI11-03-01-270: FS | CHI11-03-01-270
CHI11-03-01-295 | C03/01-DH- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | 11 | 11 | 2025-03-31 | 2025-04-11 | 0 | CHI11-03-01-270: FS, CHI11-03-01-290: SS | CHI11-03-01-270, CHI11-03-01-290
COLO 3 - CELL 1 Mechanical Gallery |  | 44 | 44 | 2025-02-13 | 2025-04-07 | 34
CHI11-03-01-105 | C03/01-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-02-13 | 2025-02-14 | 24 | CHI11-03-01-80: FS, CHI11-03-01-30: FS | CHI11-03-01-80, CHI11-03-01-30
CHI11-03-01-120 | C03/01-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-02-15 | 2025-02-17 | 24 | CHI11-03-01-105: FS | CHI11-03-01-105
CHI11-03-01-125 | C03/01-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-02-15 | 2025-02-18 | 24 | CHI11-03-01-120: SS | CHI11-03-01-120
CHI11-03-01-145 | C03/01-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-02-19 | 2025-02-25 | 24 | CHI11-03-01-125: FS | CHI11-03-01-125
CHI11-03-01-170 | C03/01-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-02-26 | 2025-03-05 | 24 | CHI11-03-01-145: FS | CHI11-03-01-145
CHI11-03-01-190 | C03/01-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-03-04 | 2025-03-05 | 24 | CHI11-03-01-170: FF, CHI11-03-01-20: FS | CHI11-03-01-170, CHI11-03-01-20
CHI11-03-01-205 | C03/01-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-03-06 | 2025-03-07 | 24 | CHI11-03-01-190: FS | CHI11-03-01-190
CHI11-03-01-210 | C03/01-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-06 | 2025-03-06 | 24 | CHI11-03-01-170: FS, CHI11-03-01-125: FF | CHI11-03-01-170, CHI11-03-01-125
CHI11-03-01-220 | C03/01-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-03-07 | 2025-03-11 | 24 | CHI11-03-01-210: FS | CHI11-03-01-210
CHI11-03-01-225 | C03/01-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-03-08 | 2025-03-10 | 24 | CHI11-03-01-205: FS | CHI11-03-01-205
CHI11-03-01-245 | C03/01-Mech Gallery- General Cleaning | 3 | 3 | 2025-03-11 | 2025-03-13 | 24 | CHI11-03-01-225: FS | CHI11-03-01-225
CHI11-03-01-250 | C03/01-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-03-12 | 2025-03-13 | 24 | CHI11-03-01-220: FS, CHI11-03-01-210: FS | CHI11-03-01-220, CHI11-03-01-210
CHI11-03-01-255 | C03/01-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-03-12 | 2025-03-24 | 38 | CHI-11-03-BAS-03: FS, CHI11-03-01-220: FS | CHI-11-03-BAS-03, CHI11-03-01-220
CHI11-03-01-265 | C03/01-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-03-14 | 2025-03-18 | 24 | CHI-11-03-AHU-03: FS, CHI-11-03-AHU-02: SS, CHI-11-03-ROJ-S: SS, CHI11-03-01-245: FS, CHI11-03-01-250: FS | CHI-11-03-AHU-03, CHI-11-03-AHU-02, CHI-11-03-ROJ-S, CHI11-03-01-245, CHI11-03-01-250
CHI11-03-01-280 | C03/01-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-03-19 | 2025-04-02 | 24 | CHI11-03-01-265: FS | CHI11-03-01-265
CHI11-03-01-285 | C03/01-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-03-25 | 2025-04-02 | 38 | CHI11-03-01-255: FS | CHI11-03-01-255
CHI11-03-01-300 | C03/01-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-04-03 | 2025-04-07 | 24 | CHI11-03-01-280: FS | CHI11-03-01-280
COLO 3- CELL 1 Punchlist |  | 10 | 10 | 2025-04-17 | 2025-04-28 | 17
CHI11-03-01-310 | C03/01- Punchlist | 10 | 10 | 2025-04-17 | 2025-04-28 | 17 | CHI11-03-01-295: FS, CHI11-03-01-305: FS, CHI11-03-01-300: FS, CHI11-03-01-235: FS | CHI11-03-01-295, CHI11-03-01-305, CHI11-03-01-300, CHI11-03-01-235
COLO 3 - CELL 2 |  | 94 | 94 | 2025-01-29 | 2025-05-23 | 11
COLO 3 - CELL 2 Data Hall |  | 84 | 84 | 2025-01-29 | 2025-05-12 | 11
CHI11-03-02-10 | C03/02-DH- Layout Framing | 1 | 1 | 2025-01-29 | 2025-01-29 | 0 | CHI11-03-01-35: SS, CHI11-03-01-15: FS | CHI11-03-01-35, CHI11-03-01-15
CHI11-03-02-15 | C03/02-DH- Install Framing | 3 | 3 | 2025-01-30 | 2025-02-01 | 0 | CHI11-03-02-10: FS | CHI11-03-02-10
CHI11-03-02-20 | C03/02-DH- In-Wall R/I | 3 | 3 | 2025-02-03 | 2025-02-05 | 0 | CHI11-03-02-15: FS | CHI11-03-02-15
CHI11-03-02-35 | C03/02-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-02-06 | 2025-02-10 | 41 | CHI11-03-02-20: FS | CHI11-03-02-20
CHI11-03-02-40 | C03/02-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-02-06 | 2025-02-10 | 0 | CHI11-03-02-20: FS | CHI11-03-02-20
CHI11-03-02-55 | C03/02-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-02-11 | 2025-02-13 | 46 | CHI11-03-02-35: FS | CHI11-03-02-35
CHI11-03-02-60 | C03/02-DH- Overhead R/I - Electrical | 4 | 4 | 2025-02-11 | 2025-02-14 | 46 | CHI11-03-02-55: SS | CHI11-03-02-55
CHI11-03-02-65 | C03/02-DH- Finish Dry-Wall | 3 | 3 | 2025-02-11 | 2025-02-13 | 41 | CHI11-03-02-40: FS | CHI11-03-02-40
CHI11-03-02-85 | C03/02-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-02-13 | 2025-02-14 | 46 | CHI11-03-02-60: FF | CHI11-03-02-60
CHI11-03-02-90 | C03/02-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-02-13 | 2025-02-14 | 46 | CHI11-03-02-85: FF, CHI11-03-02-60: FF | CHI11-03-02-85, CHI11-03-02-60
CHI11-03-02-115 | C03/02-DH- Paint Dry-Wall | 3 | 3 | 2025-02-14 | 2025-02-17 | 41 | CHI11-03-02-65: FS | CHI11-03-02-65
CHI11-03-02-135 | C03/02-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-02-18 | 2025-02-20 | 41 | CHI11-03-02-115: FS | CHI11-03-02-115
CHI11-03-02-145 | C03/02-DH- Install Secondary Steel | 2 | 2 | 2025-02-21 | 2025-02-22 | 41 | CHI11-03-02-90: FS, CHI11-03-02-135: FS | CHI11-03-02-90, CHI11-03-02-135
CHI11-03-02-150 | C03/02-DH- Paint Secondary Steel | 2 | 2 | 2025-02-24 | 2025-02-25 | 41 | CHI11-03-02-145: FS | CHI11-03-02-145
CHI11-03-02-160 | C03/02-DH- General Cleaning | 1 | 1 | 2025-02-26 | 2025-02-26 | 44 | CHI11-03-02-150: FS | CHI11-03-02-150
CHI11-03-02-165 | C03/02-DH- Install Ceiling Grid | 4 | 4 | 2025-02-26 | 2025-03-03 | 41 | CHI11-03-02-85: FS, CHI11-03-02-90: FS, CHI11-03-02-150: FS | CHI11-03-02-85, CHI11-03-02-90, CHI11-03-02-150
CHI11-03-02-175 | C03/02-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-03-04 | 2025-03-07 | 44 | CHI11-03-02-165: FS | CHI11-03-02-165
CHI11-03-02-180 | C03/02-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-03-04 | 2025-03-08 | 41 | CHI-11-03-HAC-03: FS, CHI11-03-02-165: FS, CHI11-03-02-160: FS | CHI-11-03-HAC-03, CHI11-03-02-165, CHI11-03-02-160
CHI11-03-02-200 | C03/02-DH- Install Busways on HAC Arms | 5 | 5 | 2025-03-06 | 2025-03-11 | 41 | CHI11-03-02-180: FF 2 | CHI11-03-02-180
CHI11-03-02-210 | C03/02-DH- Install Device Tiles | 2 | 2 | 2025-03-08 | 2025-03-10 | 44 | CHI11-03-02-175: FS | CHI11-03-02-175
CHI11-03-02-215 | C03/02-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-03-08 | 2025-03-13 | 41 | CHI11-03-02-200: FF 2 | CHI11-03-02-200
CHI11-03-02-220 | C03/02-DH- Set PDUs | 4 | 4 | 2025-03-08 | 2025-03-12 | 49 | CHI11-03-02-175: FS | CHI11-03-02-175
CHI11-03-02-245 | C03/02-DH- Raise HACs | 4 | 4 | 2025-03-14 | 2025-03-18 | 41 | CHI11-03-02-210: FS, CHI11-03-02-215: FS | CHI11-03-02-210, CHI11-03-02-215
CHI11-03-02-260 | C03/02-DH- Detail HACs | 4 | 4 | 2025-03-19 | 2025-03-24 | 51 | CHI11-03-02-245: FS | CHI11-03-02-245
CHI11-03-02-265 | C03/02-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-03-19 | 2025-03-21 | 41 | CHI11-03-02-245: FS | CHI11-03-02-245
CHI11-03-02-275 | C03/02-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-03-24 | 2025-03-26 | 41 | CHI11-03-02-220: FS, CHI11-03-02-265: FS | CHI11-03-02-220, CHI11-03-02-265
CHI11-03-02-285 | C03/02-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-03-27 | 2025-04-01 | 41 | CHI11-03-02-275: FS | CHI11-03-02-275
CHI11-03-02-310 | C03/02-DH- Terminate PDUs | 3 | 3 | 2025-05-09 | 2025-05-12 | 11 | CHI11-03-02-285: FS, CHI11-03-02-305: FS | CHI11-03-02-285, CHI11-03-02-305
COLO 3 - CELL 2 Electrical Room |  | 77 | 77 | 2025-02-03 | 2025-05-08 | 0
CHI11-03-02-25 | C03/02-Elec Rm- Install Framing | 2 | 2 | 2025-02-03 | 2025-02-04 | 39 | CHI11-03-02-15: FS | CHI11-03-02-15
CHI11-03-02-30 | C03/02-Elec Rm- In-Wall R/I | 2 | 2 | 2025-02-05 | 2025-02-06 | 39 | CHI11-03-02-25: FS | CHI11-03-02-25
CHI11-03-02-45 | C03/02-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-02-07 | 2025-02-10 | 41 | CHI11-03-02-30: FS | CHI11-03-02-30
CHI11-03-02-50 | C03/02-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-02-07 | 2025-02-12 | 39 | CHI11-03-02-30: FS | CHI11-03-02-30
CHI11-03-02-70 | C03/02-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-02-11 | 2025-02-12 | 41 | CHI11-03-02-45: FS | CHI11-03-02-45
CHI11-03-02-75 | C03/02-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-02-11 | 2025-02-13 | 41 | CHI11-03-02-70: SS | CHI11-03-02-70
CHI11-03-02-95 | C03/02-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-02-13 | 2025-02-14 | 39 | CHI11-03-02-50: FS | CHI11-03-02-50
CHI11-03-02-100 | C03/02-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-02-13 | 2025-02-13 | 41 | CHI11-03-02-75: FF | CHI11-03-02-75
CHI11-03-02-120 | C03/02-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-02-14 | 2025-02-15 | 41 | CHI11-03-02-100: FS | CHI11-03-02-100
CHI11-03-02-125 | C03/02-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-02-15 | 2025-02-17 | 39 | CHI11-03-02-95: FS | CHI11-03-02-95
CHI11-03-02-140 | C03/02-Elec Rm- General Cleaning | 1 | 1 | 2025-02-18 | 2025-02-18 | 39 | CHI11-03-02-125: FS | CHI11-03-02-125
CHI11-03-02-250 | C03/02-Elec Rm- Set Electrical Equipments | 4 | 4 | 2025-03-17 | 2025-03-20 | 18 | CHI11-03-02-140: FS, CHI11-03-02-120: FS, CHI11-03-01-230: FS | CHI11-03-02-140, CHI11-03-02-120, CHI11-03-01-230
CHI11-03-02-295 | C03/02-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | 11 | 11 | 2025-04-14 | 2025-04-25 | 0 | CHI11-03-01-295: FS, CHI11-03-02-250: FS | CHI11-03-01-295, CHI11-03-02-250
CHI11-03-02-300 | C03/02-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-04-26 | 2025-04-30 | 0 | CHI11-03-02-295: FS | CHI11-03-02-295
CHI11-03-02-305 | C03/02-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | 10 | 10 | 2025-04-26 | 2025-05-08 | 0 | CHI11-03-02-295: FS, CHI11-03-02-300: SS | CHI11-03-02-295, CHI11-03-02-300
COLO 3 - CELL 2 Mechanical Gallery |  | 44 | 44 | 2025-02-11 | 2025-04-04 | 41
CHI11-03-02-80 | C03/02-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-02-11 | 2025-02-12 | 41 | CHI11-03-02-45: FS, CHI11-03-02-35: FS | CHI11-03-02-45, CHI11-03-02-35
CHI11-03-02-105 | C03/02-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-02-13 | 2025-02-14 | 41 | CHI11-03-02-80: FS | CHI11-03-02-80
CHI11-03-02-110 | C03/02-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-02-13 | 2025-02-15 | 41 | CHI11-03-02-105: SS | CHI11-03-02-105
CHI11-03-02-130 | C03/02-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-02-17 | 2025-02-22 | 41 | CHI11-03-02-110: FS | CHI11-03-02-110
CHI11-03-02-155 | C03/02-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-02-24 | 2025-03-03 | 41 | CHI11-03-02-130: FS | CHI11-03-02-130
CHI11-03-02-170 | C03/02-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-02-28 | 2025-03-03 | 41 | CHI11-03-02-155: FF, CHI11-03-02-20: FS | CHI11-03-02-155, CHI11-03-02-20
CHI11-03-02-185 | C03/02-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-03-04 | 2025-03-05 | 41 | CHI11-03-02-170: FS | CHI11-03-02-170
CHI11-03-02-190 | C03/02-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-04 | 2025-03-04 | 41 | CHI11-03-02-155: FS, CHI11-03-02-110: FF | CHI11-03-02-155, CHI11-03-02-110
CHI11-03-02-195 | C03/02-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-03-05 | 2025-03-08 | 41 | CHI11-03-02-190: FS | CHI11-03-02-190
CHI11-03-02-205 | C03/02-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-03-06 | 2025-03-07 | 41 | CHI11-03-02-185: FS | CHI11-03-02-185
CHI11-03-02-225 | C03/02-Mech Gallery- General Cleaning | 3 | 3 | 2025-03-08 | 2025-03-11 | 41 | CHI11-03-02-205: FS | CHI11-03-02-205
CHI11-03-02-230 | C03/02-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-03-10 | 2025-03-11 | 41 | CHI11-03-02-195: FS, CHI11-03-02-190: FS | CHI11-03-02-195, CHI11-03-02-190
CHI11-03-02-235 | C03/02-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-03-10 | 2025-03-20 | 45 | CHI11-03-02-195: FS | CHI11-03-02-195
CHI11-03-02-240 | C03/02-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-03-12 | 2025-03-15 | 41 | CHI11-03-02-225: FS, CHI11-03-02-230: FS | CHI11-03-02-225, CHI11-03-02-230
CHI11-03-02-255 | C03/02-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-03-17 | 2025-03-31 | 41 | CHI11-03-02-240: FS | CHI11-03-02-240
CHI11-03-02-270 | C03/02-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-03-21 | 2025-03-31 | 45 | CHI11-03-02-235: FS | CHI11-03-02-235
CHI11-03-02-290 | C03/02-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-04-01 | 2025-04-04 | 41 | CHI11-03-02-255: FS | CHI11-03-02-255
COLO 3 - CELL 2 Punchlist |  | 10 | 10 | 2025-05-13 | 2025-05-23 | 11
CHI11-03-02-280 | C03/C02- Punchlist | 10 | 10 | 2025-05-13 | 2025-05-23 | 11 | CHI11-03-02-290: FS, CHI11-03-02-305: FS, CHI11-03-02-310: FS, CHI11-03-02-210: FS, CHI11-03-02-260: FS | CHI11-03-02-290, CHI11-03-02-305, CHI11-03-02-310, CHI11-03-02-210, CHI11-03-02-260
COLO 3 - CELL 3 |  | 96 | 96 | 2025-02-21 | 2025-06-20 | 0
COLO 3 - CELL 3 Data Hall |  | 86 | 86 | 2025-02-21 | 2025-06-07 | 0
CHI11-03-03-10 | C03/03-DH- Layout Framing | 1 | 1 | 2025-02-21 | 2025-02-21 | 0 | CHI11-03-04-40: FS | CHI11-03-04-40
CHI11-03-03-15 | C03/03-DH- Install Framing | 3 | 3 | 2025-02-22 | 2025-02-25 | 0 | CHI11-03-03-10: FS | CHI11-03-03-10
CHI11-03-03-20 | C03/03-DH- In-Wall R/I | 3 | 3 | 2025-02-26 | 2025-02-28 | 32 | CHI11-03-03-15: FS | CHI11-03-03-15
CHI11-03-03-35 | C03/03-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-03-03 | 2025-03-05 | 32 | CHI11-03-03-20: FS | CHI11-03-03-20
CHI11-03-03-40 | C03/03-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-03-03 | 2025-03-05 | 32 | CHI11-03-03-20: FS | CHI11-03-03-20
CHI11-03-03-55 | C03/03-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-03-06 | 2025-03-08 | 37 | CHI11-03-03-35: FS | CHI11-03-03-35
CHI11-03-03-60 | C03/03-DH- Overhead R/I - Electrical | 4 | 4 | 2025-03-06 | 2025-03-10 | 37 | CHI11-03-03-55: SS | CHI11-03-03-55
CHI11-03-03-65 | C03/03-DH- Finish Dry-Wall | 3 | 3 | 2025-03-06 | 2025-03-08 | 32 | CHI11-03-03-40: FS | CHI11-03-03-40
CHI11-03-03-85 | C03/03-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-03-08 | 2025-03-10 | 37 | CHI11-03-03-60: FF | CHI11-03-03-60
CHI11-03-03-90 | C03/03-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-03-08 | 2025-03-10 | 37 | CHI11-03-03-85: FF, CHI11-03-03-60: FF | CHI11-03-03-85, CHI11-03-03-60
CHI11-03-03-115 | C03/03-DH- Paint Dry-Wall | 3 | 3 | 2025-03-10 | 2025-03-12 | 32 | CHI11-03-03-65: FS | CHI11-03-03-65
CHI11-03-03-135 | C03/03-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-03-13 | 2025-03-15 | 32 | CHI11-03-03-115: FS | CHI11-03-03-115
CHI11-03-03-150 | C03/03-DH- Install Secondary Steel | 2 | 2 | 2025-03-17 | 2025-03-18 | 32 | CHI11-03-03-90: FS, CHI11-03-03-135: FS | CHI11-03-03-90, CHI11-03-03-135
CHI11-03-03-155 | C03/03-DH- Paint Secondary Steel | 2 | 2 | 2025-03-19 | 2025-03-20 | 32 | CHI11-03-03-150: FS | CHI11-03-03-150
CHI11-03-03-165 | C03/03-DH- General Cleaning | 1 | 1 | 2025-03-21 | 2025-03-21 | 35 | CHI11-03-03-155: FS | CHI11-03-03-155
CHI11-03-03-170 | C03/03-DH- Install Ceiling Grid | 4 | 4 | 2025-03-21 | 2025-03-26 | 32 | CHI11-03-03-85: FS, CHI11-03-03-90: FS, CHI11-03-03-155: FS | CHI11-03-03-85, CHI11-03-03-90, CHI11-03-03-155
CHI11-03-03-180 | C03/03-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-03-27 | 2025-03-31 | 35 | CHI11-03-03-170: FS | CHI11-03-03-170
CHI11-03-03-185 | C03/03-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-03-27 | 2025-04-01 | 32 | CHI11-03-03-170: FS, CHI11-03-03-165: FS | CHI11-03-03-170, CHI11-03-03-165
CHI11-03-03-205 | C03/03-DH- Install Busways on HAC Arms | 5 | 5 | 2025-03-29 | 2025-04-03 | 32 | CHI11-03-03-185: FF 2 | CHI11-03-03-185
CHI11-03-03-215 | C03/03-DH- Install Device Tiles | 2 | 2 | 2025-04-01 | 2025-04-02 | 35 | CHI11-03-03-180: FS | CHI11-03-03-180
CHI11-03-03-220 | C03/03-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-04-01 | 2025-04-05 | 32 | CHI11-03-03-205: FF 2 | CHI11-03-03-205
CHI11-03-03-225 | C03/03-DH- Set PDUs | 4 | 4 | 2025-04-01 | 2025-04-04 | 40 | CHI11-03-03-180: FS | CHI11-03-03-180
CHI11-03-03-250 | C03/03-DH- Raise HACs | 4 | 4 | 2025-04-07 | 2025-04-10 | 32 | CHI11-03-03-215: FS, CHI11-03-03-220: FS | CHI11-03-03-215, CHI11-03-03-220
CHI11-03-03-260 | C03/03-DH- Detail HACs | 4 | 4 | 2025-04-11 | 2025-04-16 | 42 | CHI11-03-03-250: FS | CHI11-03-03-250
CHI11-03-03-265 | C03/03-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-04-11 | 2025-04-15 | 32 | CHI11-03-03-250: FS | CHI11-03-03-250
CHI11-03-03-275 | C03/03-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-04-16 | 2025-04-18 | 32 | CHI11-03-03-225: FS, CHI11-03-03-265: FS | CHI11-03-03-225, CHI11-03-03-265
CHI11-03-03-285 | C03/03-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-04-19 | 2025-04-24 | 32 | CHI11-03-03-275: FS | CHI11-03-03-275
CHI11-03-03-310 | C03/03-DH- Terminate PDUs | 3 | 3 | 2025-06-05 | 2025-06-07 | 0 | CHI11-03-03-285: FS, CHI11-03-03-305: FS | CHI11-03-03-285, CHI11-03-03-305
COLO 3 - CELL 3 Electrical Room |  | 79 | 79 | 2025-02-26 | 2025-06-04 | 0
CHI11-03-03-25 | C03/03-Elec Rm- Install Framing | 2 | 2 | 2025-02-26 | 2025-02-27 | 32 | CHI11-03-03-15: FS | CHI11-03-03-15
CHI11-03-03-30 | C03/03-Elec Rm- In-Wall R/I | 2 | 2 | 2025-02-28 | 2025-03-03 | 32 | CHI11-03-03-25: FS | CHI11-03-03-25
CHI11-03-03-45 | C03/03-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-03-04 | 2025-03-05 | 32 | CHI11-03-03-30: FS | CHI11-03-03-30
CHI11-03-03-50 | C03/03-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-03-04 | 2025-03-07 | 42 | CHI11-03-03-30: FS | CHI11-03-03-30
CHI11-03-03-70 | C03/03-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-03-06 | 2025-03-07 | 44 | CHI11-03-03-45: FS | CHI11-03-03-45
CHI11-03-03-75 | C03/03-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-03-06 | 2025-03-08 | 44 | CHI11-03-03-70: SS | CHI11-03-03-70
CHI11-03-03-95 | C03/03-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-03-08 | 2025-03-10 | 42 | CHI11-03-03-50: FS | CHI11-03-03-50
CHI11-03-03-100 | C03/03-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-08 | 2025-03-08 | 44 | CHI11-03-03-75: FF | CHI11-03-03-75
CHI11-03-03-120 | C03/03-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-03-10 | 2025-03-11 | 44 | CHI11-03-03-100: FS | CHI11-03-03-100
CHI11-03-03-125 | C03/03-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-03-11 | 2025-03-12 | 42 | CHI11-03-03-95: FS | CHI11-03-03-95
CHI11-03-03-140 | C03/03-Elec Rm- General Cleaning | 1 | 1 | 2025-03-13 | 2025-03-13 | 42 | CHI11-03-03-125: FS | CHI11-03-03-125
CHI11-03-03-145 | C03/03-Elec Rm- Set Electrical Equipments | 4 | 4 | 2025-03-14 | 2025-03-18 | 42 | CHI11-03-03-140: FS, CHI11-03-03-120: FS | CHI11-03-03-140, CHI11-03-03-120
CHI11-03-03-295 | C03/03-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | 11 | 11 | 2025-05-10 | 2025-05-22 | 0 | CHI11-03-04-305: FS, CHI11-03-03-145: FS | CHI11-03-04-305, CHI11-03-03-145
CHI11-03-03-300 | C03/03-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 3 | 3 | 2025-05-23 | 2025-05-28 | 0 | CHI11-03-03-295: FS | CHI11-03-03-295
CHI11-03-03-305 | C03/03-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | 9 | 9 | 2025-05-23 | 2025-06-04 | 0 | CHI11-03-03-295: FS, CHI11-03-03-300: SS | CHI11-03-03-295, CHI11-03-03-300
COLO 3 - CELL 3 Mechanical Gallery |  | 44 | 44 | 2025-03-06 | 2025-04-28 | 32
CHI11-03-03-80 | C03/03-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-03-06 | 2025-03-07 | 32 | CHI11-03-03-45: FS, CHI11-03-03-35: FS | CHI11-03-03-45, CHI11-03-03-35
CHI11-03-03-105 | C03/03-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-03-08 | 2025-03-10 | 32 | CHI11-03-03-80: FS | CHI11-03-03-80
CHI11-03-03-110 | C03/03-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-03-08 | 2025-03-11 | 32 | CHI11-03-03-105: SS | CHI11-03-03-105
CHI11-03-03-130 | C03/03-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-03-12 | 2025-03-18 | 32 | CHI11-03-03-110: FS | CHI11-03-03-110
CHI11-03-03-160 | C03/03-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-03-19 | 2025-03-26 | 32 | CHI11-03-03-130: FS | CHI11-03-03-130
CHI11-03-03-175 | C03/03-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-03-25 | 2025-03-26 | 32 | CHI11-03-03-160: FF, CHI11-03-03-20: FS | CHI11-03-03-160, CHI11-03-03-20
CHI11-03-03-190 | C03/03-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-03-27 | 2025-03-28 | 32 | CHI11-03-03-175: FS | CHI11-03-03-175
CHI11-03-03-195 | C03/03-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-27 | 2025-03-27 | 32 | CHI11-03-03-160: FS, CHI11-03-03-110: FF | CHI11-03-03-160, CHI11-03-03-110
CHI11-03-03-200 | C03/03-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-03-28 | 2025-04-01 | 32 | CHI11-03-03-195: FS | CHI11-03-03-195
CHI11-03-03-210 | C03/03-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-03-29 | 2025-03-31 | 32 | CHI11-03-03-190: FS | CHI11-03-03-190
CHI11-03-03-230 | C03/03-Mech Gallery- General Cleaning | 3 | 3 | 2025-04-01 | 2025-04-03 | 32 | CHI11-03-03-210: FS | CHI11-03-03-210
CHI11-03-03-235 | C03/03-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-04-02 | 2025-04-03 | 32 | CHI11-03-03-200: FS, CHI11-03-03-195: FS | CHI11-03-03-200, CHI11-03-03-195
CHI11-03-03-240 | C03/03-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-04-02 | 2025-04-14 | 36 | CHI11-03-03-200: FS | CHI11-03-03-200
CHI11-03-03-245 | C03/03-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-04-04 | 2025-04-08 | 32 | CHI11-03-03-230: FS, CHI11-03-03-235: FS | CHI11-03-03-230, CHI11-03-03-235
CHI11-03-03-255 | C03/03-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-04-09 | 2025-04-23 | 32 | CHI11-03-03-245: FS | CHI11-03-03-245
CHI11-03-03-270 | C03/03-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-04-15 | 2025-04-23 | 36 | CHI11-03-03-240: FS | CHI11-03-03-240
CHI11-03-03-290 | C03/03-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-04-24 | 2025-04-28 | 32 | CHI11-03-03-255: FS | CHI11-03-03-255
COLO 3 - CELL 3 Punchlist |  | 10 | 10 | 2025-06-09 | 2025-06-20 | 0
CHI11-03-03-280 | C03/03- Punchlist | 10 | 10 | 2025-06-09 | 2025-06-20 | 0 | CHI11-03-03-290: FS, CHI11-03-03-305: FS, CHI11-03-03-310: FS, CHI11-03-03-215: FS, CHI11-03-03-260: FS | CHI11-03-03-290, CHI11-03-03-305, CHI11-03-03-310, CHI11-03-03-215, CHI11-03-03-260
COLO 3 - CELL 4 |  | 83 | 83 | 2025-02-10 | 2025-05-21 | 8
COLO 3 - CELL 4 Data Hall |  | 76 | 76 | 2025-02-10 | 2025-05-13 | 10
CHI11-03-04-10 | C03/04-DH- Layout Framing | 1 | 1 | 2025-02-10 | 2025-02-10 | 0 | CHI11-03-02-40: SS 2 | CHI11-03-02-40
CHI11-03-04-15 | C03/04-DH- Install Framing | 3 | 3 | 2025-02-11 | 2025-02-13 | 0 | CHI11-03-04-10: FS | CHI11-03-04-10
CHI11-03-04-20 | C03/04-DH- In-Wall R/I | 3 | 3 | 2025-02-14 | 2025-02-17 | 0 | CHI11-03-04-15: FS | CHI11-03-04-15
CHI11-03-04-35 | C03/04-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-02-18 | 2025-02-20 | 27 | CHI11-03-04-20: FS | CHI11-03-04-20
CHI11-03-04-40 | C03/04-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-02-18 | 2025-02-20 | 0 | CHI11-03-04-20: FS | CHI11-03-04-20
CHI11-03-04-55 | C03/04-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-02-21 | 2025-02-24 | 37 | CHI11-03-04-35: FS | CHI11-03-04-35
CHI11-03-04-60 | C03/04-DH- Overhead R/I - Electrical | 4 | 4 | 2025-02-21 | 2025-02-25 | 37 | CHI11-03-04-55: SS | CHI11-03-04-55
CHI11-03-04-65 | C03/04-DH- Finish Dry-Wall | 3 | 3 | 2025-02-21 | 2025-02-24 | 32 | CHI11-03-04-40: FS | CHI11-03-04-40
CHI11-03-04-85 | C03/04-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-02-24 | 2025-02-25 | 37 | CHI11-03-04-60: FF | CHI11-03-04-60
CHI11-03-04-90 | C03/04-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-02-24 | 2025-02-25 | 37 | CHI11-03-04-85: FF, CHI11-03-04-60: FF | CHI11-03-04-85, CHI11-03-04-60
CHI11-03-04-115 | C03/04-DH- Paint Dry-Wall | 3 | 3 | 2025-02-25 | 2025-02-27 | 32 | CHI11-03-04-65: FS | CHI11-03-04-65
CHI11-03-04-135 | C03/04-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-02-28 | 2025-03-04 | 32 | CHI11-03-04-115: FS | CHI11-03-04-115
CHI11-03-04-150 | C03/04-DH- Install Secondary Steel | 2 | 2 | 2025-03-05 | 2025-03-06 | 32 | CHI11-03-04-90: FS, CHI11-03-04-135: FS | CHI11-03-04-90, CHI11-03-04-135
CHI11-03-04-155 | C03/04-DH- Paint Secondary Steel | 2 | 2 | 2025-03-07 | 2025-03-08 | 32 | CHI11-03-04-150: FS | CHI11-03-04-150
CHI11-03-04-170 | C03/04-DH- General Cleaning | 1 | 1 | 2025-03-10 | 2025-03-10 | 35 | CHI11-03-04-155: FS | CHI11-03-04-155
CHI11-03-04-175 | C03/04-DH- Install Ceiling Grid | 4 | 4 | 2025-03-10 | 2025-03-13 | 32 | CHI11-03-04-85: FS, CHI11-03-04-90: FS, CHI11-03-04-155: FS | CHI11-03-04-85, CHI11-03-04-90, CHI11-03-04-155
CHI11-03-04-185 | C03/04-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-03-14 | 2025-03-18 | 35 | CHI11-03-04-175: FS | CHI11-03-04-175
CHI11-03-04-190 | C03/04-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-03-14 | 2025-03-19 | 32 | CHI11-03-04-175: FS, CHI11-03-04-170: FS | CHI11-03-04-175, CHI11-03-04-170
CHI11-03-04-210 | C03/04-DH- Install Busways on HAC Arms | 5 | 5 | 2025-03-17 | 2025-03-21 | 32 | CHI11-03-04-190: FF 2 | CHI11-03-04-190
CHI11-03-04-220 | C03/04-DH- Install Device Tiles | 2 | 2 | 2025-03-19 | 2025-03-20 | 35 | CHI11-03-04-185: FS | CHI11-03-04-185
CHI11-03-04-225 | C03/04-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-03-19 | 2025-03-25 | 32 | CHI11-03-04-210: FF 2 | CHI11-03-04-210
CHI11-03-04-230 | C03/04-DH- Set PDUs | 4 | 4 | 2025-03-19 | 2025-03-24 | 40 | CHI11-03-04-185: FS | CHI11-03-04-185
CHI11-03-04-260 | C03/04-DH- Raise HACs | 4 | 4 | 2025-03-26 | 2025-03-29 | 32 | CHI11-03-04-220: FS, CHI11-03-04-225: FS | CHI11-03-04-220, CHI11-03-04-225
CHI11-03-04-270 | C03/04-DH- Detail HACs | 4 | 4 | 2025-03-31 | 2025-04-03 | 37 | CHI11-03-04-260: FS | CHI11-03-04-260
CHI11-03-04-275 | C03/04-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-03-31 | 2025-04-02 | 32 | CHI11-03-04-260: FS | CHI11-03-04-260
CHI11-03-04-285 | C03/04-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-04-03 | 2025-04-05 | 32 | CHI11-03-04-230: FS, CHI11-03-04-275: FS | CHI11-03-04-230, CHI11-03-04-275
CHI11-03-04-295 | C03/04-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-04-07 | 2025-04-11 | 32 | CHI11-03-04-285: FS | CHI11-03-04-285
CHI11-03-04-310 | C03/04-DH- Terminate PDUs | 3 | 3 | 2025-05-10 | 2025-05-13 | 10 | CHI11-03-04-295: FS, CHI11-03-04-305: FS | CHI11-03-04-295, CHI11-03-04-305
COLO 3 - CELL 4 Electrical Room |  | 69 | 69 | 2025-02-14 | 2025-05-09 | 0
CHI11-03-04-25 | C03/04-Elec Rm- Install Framing | 2 | 2 | 2025-02-14 | 2025-02-15 | 27 | CHI11-03-04-15: FS | CHI11-03-04-15
CHI11-03-04-30 | C03/04-Elec Rm- In-Wall R/I | 2 | 2 | 2025-02-17 | 2025-02-18 | 27 | CHI11-03-04-25: FS | CHI11-03-04-25
CHI11-03-04-45 | C03/04-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-02-19 | 2025-02-20 | 27 | CHI11-03-04-30: FS | CHI11-03-04-30
CHI11-03-04-50 | C03/04-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-02-19 | 2025-02-22 | 30 | CHI11-03-04-30: FS | CHI11-03-04-30
CHI11-03-04-70 | C03/04-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-02-21 | 2025-02-22 | 32 | CHI11-03-04-45: FS | CHI11-03-04-45
CHI11-03-04-75 | C03/04-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-02-21 | 2025-02-24 | 32 | CHI11-03-04-70: SS | CHI11-03-04-70
CHI11-03-04-95 | C03/04-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-02-24 | 2025-02-25 | 30 | CHI11-03-04-50: FS | CHI11-03-04-50
CHI11-03-04-100 | C03/04-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-02-24 | 2025-02-24 | 32 | CHI11-03-04-75: FF | CHI11-03-04-75
CHI11-03-04-120 | C03/04-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-02-25 | 2025-02-26 | 32 | CHI11-03-04-100: FS | CHI11-03-04-100
CHI11-03-04-125 | C03/04-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-02-26 | 2025-02-27 | 30 | CHI11-03-04-95: FS | CHI11-03-04-95
CHI11-03-04-140 | C03/04-Elec Rm- General Cleaning | 1 | 1 | 2025-02-28 | 2025-02-28 | 30 | CHI11-03-04-125: FS | CHI11-03-04-125
CHI11-03-04-145 | C03/04-Elec Rm- Set Electrical Equipments | 4 | 4 | 2025-03-03 | 2025-03-06 | 30 | CHI11-03-04-140: FS, CHI11-03-04-120: FS | CHI11-03-04-140, CHI11-03-04-120
CHI11-03-04-160 | C03/04-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | 11 | 11 | 2025-03-07 | 2025-03-19 | 30 | CHI11-03-04-145: FS | CHI11-03-04-145
CHI11-03-04-240 | C03/04-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-03-20 | 2025-03-25 | 30 | CHI11-03-04-160: FS | CHI11-03-04-160
CHI11-03-04-305 | C03/04-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | 11 | 11 | 2025-04-26 | 2025-05-09 | 0 | CHI11-03-02-305: SS, CHI11-03-04-160: FS, CHI11-03-04-240: SS | CHI11-03-02-305, CHI11-03-04-160, CHI11-03-04-240
COLO 3 - CELL 4 Mechanical Gallery |  | 44 | 44 | 2025-02-21 | 2025-04-16 | 37
CHI11-03-04-80 | C03/04-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-02-21 | 2025-02-22 | 27 | CHI11-03-04-45: FS, CHI11-03-04-35: FS | CHI11-03-04-45, CHI11-03-04-35
CHI11-03-04-105 | C03/04-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-02-24 | 2025-02-25 | 27 | CHI11-03-04-80: FS | CHI11-03-04-80
CHI11-03-04-110 | C03/04-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-02-24 | 2025-02-26 | 27 | CHI11-03-04-105: SS | CHI11-03-04-105
CHI11-03-04-130 | C03/04-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-02-27 | 2025-03-06 | 27 | CHI11-03-04-110: FS | CHI11-03-04-110
CHI11-03-04-165 | C03/04-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-03-07 | 2025-03-13 | 27 | CHI11-03-04-130: FS | CHI11-03-04-130
CHI11-03-04-180 | C03/04-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-03-12 | 2025-03-13 | 27 | CHI11-03-04-165: FF, CHI11-03-04-20: FS | CHI11-03-04-165, CHI11-03-04-20
CHI11-03-04-195 | C03/04-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-03-14 | 2025-03-15 | 27 | CHI11-03-04-180: FS | CHI11-03-04-180
CHI11-03-04-200 | C03/04-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-14 | 2025-03-14 | 27 | CHI11-03-04-165: FS, CHI11-03-04-110: FF | CHI11-03-04-165, CHI11-03-04-110
CHI11-03-04-205 | C03/04-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-03-15 | 2025-03-19 | 27 | CHI11-03-04-200: FS | CHI11-03-04-200
CHI11-03-04-215 | C03/04-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-03-17 | 2025-03-18 | 27 | CHI11-03-04-195: FS | CHI11-03-04-195
CHI11-03-04-235 | C03/04-Mech Gallery- General Cleaning | 3 | 3 | 2025-03-19 | 2025-03-21 | 27 | CHI11-03-04-215: FS | CHI11-03-04-215
CHI11-03-04-245 | C03/04-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-03-20 | 2025-03-21 | 27 | CHI11-03-04-205: FS, CHI11-03-04-200: FS | CHI11-03-04-205, CHI11-03-04-200
CHI11-03-04-250 | C03/04-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-03-20 | 2025-04-01 | 41 | CHI11-03-04-205: FS | CHI11-03-04-205
CHI11-03-04-255 | C03/04-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-03-24 | 2025-03-27 | 27 | CHI11-03-04-235: FS, CHI11-03-04-245: FS | CHI11-03-04-235, CHI11-03-04-245
CHI11-03-04-265 | C03/04-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-03-28 | 2025-04-10 | 27 | CHI11-03-04-255: FS | CHI11-03-04-255
CHI11-03-04-280 | C03/04-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-04-02 | 2025-04-10 | 41 | CHI11-03-04-250: FS | CHI11-03-04-250
CHI11-03-04-300 | C03/04-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-04-11 | 2025-04-16 | 27 | CHI11-03-04-265: FS | CHI11-03-04-265
COLO 3 - CELL 4 Punchlist |  | 10 | 10 | 2025-05-10 | 2025-05-21 | 8
CHI11-03-04-290 | C03/04- Punchlist | 10 | 10 | 2025-05-10 | 2025-05-21 | 8 | CHI11-03-04-300: FS, CHI11-03-04-305: FS, CHI11-03-04-310: FF 5, CHI11-03-04-220: FS, CHI11-03-04-270: FS | CHI11-03-04-300, CHI11-03-04-305, CHI11-03-04-310, CHI11-03-04-220, CHI11-03-04-270
COLO 4 |  | 128 | 128 | 2025-02-24 | 2025-08-02 | 5
COLO 4 - CELL 1 |  | 67 | 67 | 2025-02-24 | 2025-05-16 | 30
COLO 4 - CELL 1 Data Hall |  | 57 | 57 | 2025-02-24 | 2025-05-05 | 30
CHI11-04-01-10 | C04/01-DH- Layout Framing | 1 | 1 | 2025-02-24 | 2025-02-24 | 0 | CHI11-03-03-15: SS 1, CHI11-04-C&S-30: FS, CHI-11-04-DRY-F: FS | CHI11-03-03-15, CHI11-04-C&S-30, CHI-11-04-DRY-F
CHI11-04-01-15 | C04/01-DH- IInstall Framing | 3 | 3 | 2025-02-25 | 2025-02-27 | 0 | CHI11-04-01-10: FS | CHI11-04-01-10
CHI11-04-01-20 | C04/01-DH- In-Wall R/I | 3 | 3 | 2025-02-28 | 2025-03-04 | 0 | CHI11-04-01-15: FS | CHI11-04-01-15
CHI11-04-01-35 | C04/01-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-03-05 | 2025-03-07 | 5 | CHI11-04-01-20: FS | CHI11-04-01-20
CHI11-04-01-40 | C04/01-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-03-05 | 2025-03-07 | 0 | CHI11-04-01-20: FS | CHI11-04-01-20
CHI11-04-01-55 | C04/01-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-03-08 | 2025-03-11 | 5 | CHI11-04-01-35: FS | CHI11-04-01-35
CHI11-04-01-60 | C04/01-DH- Overhead R/I - Electrical | 4 | 4 | 2025-03-08 | 2025-03-12 | 5 | CHI11-04-01-55: SS | CHI11-04-01-55
CHI11-04-01-65 | C04/01-DH- Finish Dry-Wall | 3 | 3 | 2025-03-08 | 2025-03-11 | 0 | CHI11-04-01-40: FS | CHI11-04-01-40
CHI11-04-01-85 | C04/01-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-03-11 | 2025-03-12 | 5 | CHI11-04-01-60: FF | CHI11-04-01-60
CHI11-04-01-90 | C04/01-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-03-11 | 2025-03-12 | 5 | CHI11-04-01-85: FF, CHI11-04-01-60: FF | CHI11-04-01-85, CHI11-04-01-60
CHI11-04-01-115 | C04/01-DH- Paint Dry-Wall | 3 | 3 | 2025-03-12 | 2025-03-14 | 0 | CHI11-04-01-65: FS | CHI11-04-01-65
CHI11-04-01-135 | C04/01-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-03-15 | 2025-03-18 | 0 | CHI11-04-01-115: FS | CHI11-04-01-115
CHI11-04-01-145 | C04/01-DH- Install Secondary Steel | 2 | 2 | 2025-03-19 | 2025-03-20 | 0 | CHI11-04-01-90: FS, CHI11-04-01-135: FS | CHI11-04-01-90, CHI11-04-01-135
CHI11-04-01-150 | C04/01-DH- Paint Secondary Steel | 2 | 2 | 2025-03-21 | 2025-03-24 | 0 | CHI11-04-01-145: FS | CHI11-04-01-145
CHI11-04-01-160 | C04/01-DH- General Cleaning | 1 | 1 | 2025-03-25 | 2025-03-25 | 0 | CHI11-04-01-150: FS | CHI11-04-01-150
CHI11-04-01-165 | C04/01-DH- Install Ceiling Grid | 4 | 4 | 2025-03-25 | 2025-03-28 | 29 | CHI11-04-01-85: FS, CHI11-04-01-90: FS, CHI11-04-01-150: FS | CHI11-04-01-85, CHI11-04-01-90, CHI11-04-01-150
CHI11-04-01-175 | C04/01-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-03-29 | 2025-04-02 | 32 | CHI11-04-01-165: FS | CHI11-04-01-165
CHI11-04-01-180 | C04/01-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-03-29 | 2025-04-03 | 29 | CHI-11-04-HAC-03: FS, CHI-11-04-HAC-01: FS, CHI11-04-01-165: FS, CHI11-04-01-160: FS | CHI-11-04-HAC-03, CHI-11-04-HAC-01, CHI11-04-01-165, CHI11-04-01-160
CHI11-04-01-205 | C04/01-DH- Install Busways on HAC Arms | 5 | 5 | 2025-04-01 | 2025-04-05 | 29 | CHI-11-04-BUS-03: FS, CHI11-04-01-180: FF 2 | CHI-11-04-BUS-03, CHI11-04-01-180
CHI11-04-01-215 | C04/01-DH- Install Device Tiles | 2 | 2 | 2025-04-03 | 2025-04-04 | 32 | CHI11-04-01-175: FS | CHI11-04-01-175
CHI11-04-01-220 | C04/01-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-04-03 | 2025-04-08 | 29 | CHI11-04-01-205: FF 2 | CHI11-04-01-205
CHI11-04-01-225 | C04/01-DH- Set PDUs | 4 | 4 | 2025-04-03 | 2025-04-07 | 37 | CHI-11-04-PDU-03: FS, CHI11-04-01-175: FS | CHI-11-04-PDU-03, CHI11-04-01-175
CHI11-04-01-255 | C04/01-DH- Raise HACs | 4 | 4 | 2025-04-09 | 2025-04-14 | 29 | CHI11-04-01-215: FS, CHI11-04-01-220: FS | CHI11-04-01-215, CHI11-04-01-220
CHI11-04-01-265 | C04/01-DH- Detail HACs | 4 | 4 | 2025-04-15 | 2025-04-18 | 43 | CHI11-04-01-255: FS | CHI11-04-01-255
CHI11-04-01-270 | C04/01-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-04-15 | 2025-04-17 | 29 | CHI11-04-01-255: FS | CHI11-04-01-255
CHI11-04-01-280 | C04/01-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-04-18 | 2025-04-21 | 29 | CHI11-04-01-225: FS, CHI11-04-01-270: FS | CHI11-04-01-225, CHI11-04-01-270
CHI11-04-01-300 | C04/01-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-04-22 | 2025-04-26 | 29 | CHI11-04-01-280: FS | CHI11-04-01-280
CHI11-04-01-310 | C04/01-DH- Terminate PDUs | 3 | 3 | 2025-05-01 | 2025-05-05 | 26 | CHI11-04-01-300: FS, CHI11-04-01-290: FS | CHI11-04-01-300, CHI11-04-01-290
COLO 4 - CELL 1 Electrical Room |  | 50 | 50 | 2025-02-28 | 2025-04-30 | 0
CHI11-04-01-25 | C04/01-Elec Rm- Install Framing | 2 | 2 | 2025-02-28 | 2025-03-03 | 11 | CHI11-04-01-15: FS | CHI11-04-01-15
CHI11-04-01-30 | C04/01-Elec Rm- In-Wall R/I | 2 | 2 | 2025-03-04 | 2025-03-05 | 11 | CHI11-04-01-25: FS | CHI11-04-01-25
CHI11-04-01-45 | C04/01-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-03-06 | 2025-03-07 | 13 | CHI11-04-01-30: FS | CHI11-04-01-30
CHI11-04-01-50 | C04/01-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-03-06 | 2025-03-10 | 11 | CHI11-04-01-30: FS | CHI11-04-01-30
CHI11-04-01-70 | C04/01-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-03-08 | 2025-03-10 | 13 | CHI11-04-01-45: FS | CHI11-04-01-45
CHI11-04-01-75 | C04/01-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-03-08 | 2025-03-11 | 13 | CHI11-04-01-70: SS | CHI11-04-01-70
CHI11-04-01-95 | C04/01-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-03-11 | 2025-03-12 | 11 | CHI11-04-01-50: FS | CHI11-04-01-50
CHI11-04-01-100 | C04/01-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-11 | 2025-03-11 | 13 | CHI11-04-01-75: FF | CHI11-04-01-75
CHI11-04-01-120 | C04/01-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-03-12 | 2025-03-13 | 13 | CHI11-04-01-100: FS | CHI11-04-01-100
CHI11-04-01-125 | C04/01-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-03-13 | 2025-03-14 | 11 | CHI11-04-01-95: FS | CHI11-04-01-95
CHI11-04-01-140 | C04/01-Elec Rm- General Cleaning | 1 | 1 | 2025-03-15 | 2025-03-15 | 11 | CHI11-04-01-125: FS | CHI11-04-01-125
CHI11-04-01-195 | C04/01-Elec Rm- Set Electrical Equipments | 4 | 4 | 2025-03-31 | 2025-04-03 | 0 | CHI-11-04-UPS-03: FS, CHI-11-04-MSB-03: FS, CHI-11-04-LVS-03: FS, CHI-11-04-EPMS-03: FS, CHI-11-04-ADP-03: FS, CHI-11-04-ATS-03: FS, CHI-11-04-TCP-03: FS, CHI-11-04-ROJ-F: FS, CHI11-04-01-140: FS, CHI11-04-01-120: FS | CHI-11-04-UPS-03, CHI-11-04-MSB-03, CHI-11-04-LVS-03, CHI-11-04-EPMS-03, CHI-11-04-ADP-03, CHI-11-04-ATS-03, CHI-11-04-TCP-03, CHI-11-04-ROJ-F, CHI11-04-01-140, CHI11-04-01-120
CHI11-04-01-235 | C04/01-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | 11 | 11 | 2025-04-04 | 2025-04-17 | 0 | CHI11-04-01-195: FS | CHI11-04-01-195
CHI11-04-01-285 | C04/01-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-04-18 | 2025-04-22 | 0 | CHI11-04-01-235: FS | CHI11-04-01-235
CHI11-04-01-290 | C04/01-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | 11 | 11 | 2025-04-18 | 2025-04-30 | 0 | CHI11-04-01-235: FS, CHI11-04-01-285: SS | CHI11-04-01-235, CHI11-04-01-285
COLO 4 - CELL 1 Mechanical Gallery |  | 44 | 44 | 2025-03-08 | 2025-04-30 | 29
CHI11-04-01-80 | C04/01-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-03-08 | 2025-03-10 | 29 | CHI11-04-01-45: FS, CHI11-04-01-35: FS | CHI11-04-01-45, CHI11-04-01-35
CHI11-04-01-105 | C04/01-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-03-11 | 2025-03-12 | 29 | CHI11-04-01-80: FS | CHI11-04-01-80
CHI11-04-01-110 | C04/01-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-03-11 | 2025-03-13 | 29 | CHI11-04-01-105: SS | CHI11-04-01-105
CHI11-04-01-130 | C04/01-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-03-14 | 2025-03-20 | 29 | CHI11-04-01-110: FS | CHI11-04-01-110
CHI11-04-01-155 | C04/01-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-03-21 | 2025-03-28 | 29 | CHI11-04-01-130: FS | CHI11-04-01-130
CHI11-04-01-170 | C04/01-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-03-27 | 2025-03-28 | 29 | CHI11-04-01-155: FF, CHI11-04-01-20: FS | CHI11-04-01-155, CHI11-04-01-20
CHI11-04-01-185 | C04/01-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-03-29 | 2025-03-31 | 29 | CHI11-04-01-170: FS | CHI11-04-01-170
CHI11-04-01-190 | C04/01-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-29 | 2025-03-29 | 29 | CHI11-04-01-155: FS, CHI11-04-01-110: FF | CHI11-04-01-155, CHI11-04-01-110
CHI11-04-01-200 | C04/01-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-03-31 | 2025-04-03 | 29 | CHI11-04-01-190: FS | CHI11-04-01-190
CHI11-04-01-210 | C04/01-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-04-01 | 2025-04-02 | 29 | CHI11-04-01-185: FS | CHI11-04-01-185
CHI11-04-01-230 | C04/01-Mech Gallery- General Cleaning | 3 | 3 | 2025-04-03 | 2025-04-05 | 29 | CHI11-04-01-210: FS | CHI11-04-01-210
CHI11-04-01-240 | C04/01-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-04-04 | 2025-04-05 | 29 | CHI11-04-01-200: FS, CHI11-04-01-190: FS | CHI11-04-01-200, CHI11-04-01-190
CHI11-04-01-245 | C04/01-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-04-04 | 2025-04-16 | 33 | CHI-11-04-BAS-03: FS, CHI11-04-01-200: FS | CHI-11-04-BAS-03, CHI11-04-01-200
CHI11-04-01-250 | C04/01-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-04-07 | 2025-04-10 | 29 | CHI-11-04-AHU-03: FS, CHI-11-04-ROJ-S: SS, CHI11-04-01-230: FS, CHI11-04-01-240: FS | CHI-11-04-AHU-03, CHI-11-04-ROJ-S, CHI11-04-01-230, CHI11-04-01-240
CHI11-04-01-260 | C04/01-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-04-11 | 2025-04-25 | 29 | CHI11-04-01-250: FS | CHI11-04-01-250
CHI11-04-01-275 | C04/01-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-04-17 | 2025-04-25 | 33 | CHI11-04-01-245: FS | CHI11-04-01-245
CHI11-04-01-305 | C04/01-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-04-26 | 2025-04-30 | 29 | CHI11-04-01-260: FS | CHI11-04-01-260
COLO 4 - CELL 1 Punchlist |  | 10 | 10 | 2025-05-06 | 2025-05-16 | 30
CHI11-04-01-295 | C04/01- Punchlist | 10 | 10 | 2025-05-06 | 2025-05-16 | 30 | CHI11-04-01-305: FS, CHI11-04-01-290: FS, CHI11-04-01-310: FS, CHI11-04-01-215: FS, CHI11-04-01-265: FS | CHI11-04-01-305, CHI11-04-01-290, CHI11-04-01-310, CHI11-04-01-215, CHI11-04-01-265
COLO 4 - CELL 2 |  | 80 | 80 | 2025-03-05 | 2025-06-11 | 30
COLO 4 - CELL 2 Data Hall |  | 70 | 70 | 2025-03-05 | 2025-05-30 | 30
CHI11-04-02-10 | C04/02-DH- Layout Framing | 1 | 1 | 2025-03-05 | 2025-03-05 | 0 | CHI11-04-01-40: SS, CHI11-04-01-15: FS | CHI11-04-01-40, CHI11-04-01-15
CHI11-04-02-15 | C04/02-DH- Install Framing | 3 | 3 | 2025-03-06 | 2025-03-08 | 0 | CHI11-04-02-10: FS | CHI11-04-02-10
CHI11-04-02-20 | C04/02-DH- In-Wall R/I | 3 | 3 | 2025-03-10 | 2025-03-12 | 0 | CHI11-04-02-15: FS | CHI11-04-02-15
CHI11-04-02-35 | C04/02-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-03-13 | 2025-03-15 | 41 | CHI11-04-02-20: FS | CHI11-04-02-20
CHI11-04-02-40 | C04/02-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-03-13 | 2025-03-15 | 0 | CHI11-04-02-20: FS | CHI11-04-02-20
CHI11-04-02-55 | C04/02-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-03-17 | 2025-03-19 | 46 | CHI11-04-02-35: FS | CHI11-04-02-35
CHI11-04-02-60 | C04/02-DH- Overhead R/I - Electrical | 4 | 4 | 2025-03-17 | 2025-03-20 | 46 | CHI11-04-02-55: SS | CHI11-04-02-55
CHI11-04-02-65 | C04/02-DH- Finish Dry-Wall | 3 | 3 | 2025-03-17 | 2025-03-19 | 41 | CHI11-04-02-40: FS | CHI11-04-02-40
CHI11-04-02-85 | C04/02-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-03-19 | 2025-03-20 | 46 | CHI11-04-02-60: FF | CHI11-04-02-60
CHI11-04-02-90 | C04/02-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-03-19 | 2025-03-20 | 46 | CHI11-04-02-85: FF, CHI11-04-02-60: FF | CHI11-04-02-85, CHI11-04-02-60
CHI11-04-02-115 | C04/02-DH- Paint Dry-Wall | 3 | 3 | 2025-03-20 | 2025-03-24 | 41 | CHI11-04-02-65: FS | CHI11-04-02-65
CHI11-04-02-135 | C04/02-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-03-25 | 2025-03-27 | 41 | CHI11-04-02-115: FS | CHI11-04-02-115
CHI11-04-02-150 | C04/02-DH- Install Secondary Steel | 2 | 2 | 2025-03-28 | 2025-03-29 | 41 | CHI11-04-02-90: FS, CHI11-04-02-135: FS | CHI11-04-02-90, CHI11-04-02-135
CHI11-04-02-155 | C04/02-DH- Paint Secondary Steel | 2 | 2 | 2025-03-31 | 2025-04-01 | 41 | CHI11-04-02-150: FS | CHI11-04-02-150
CHI11-04-02-165 | C04/02-DH- General Cleaning | 1 | 1 | 2025-04-02 | 2025-04-02 | 44 | CHI11-04-02-155: FS | CHI11-04-02-155
CHI11-04-02-170 | C04/02-DH- Install Ceiling Grid | 4 | 4 | 2025-04-02 | 2025-04-05 | 41 | CHI11-04-02-85: FS, CHI11-04-02-90: FS, CHI11-04-02-155: FS | CHI11-04-02-85, CHI11-04-02-90, CHI11-04-02-155
CHI11-04-02-180 | C04/02-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-04-07 | 2025-04-10 | 44 | CHI11-04-02-170: FS | CHI11-04-02-170
CHI11-04-02-185 | C04/02-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-04-07 | 2025-04-11 | 41 | CHI11-04-02-170: FS, CHI11-04-02-165: FS | CHI11-04-02-170, CHI11-04-02-165
CHI11-04-02-205 | C04/02-DH- Install Busways on HAC Arms | 5 | 5 | 2025-04-09 | 2025-04-15 | 41 | CHI11-04-02-185: FF 2 | CHI11-04-02-185
CHI11-04-02-215 | C04/02-DH- Install Device Tiles | 2 | 2 | 2025-04-11 | 2025-04-14 | 44 | CHI11-04-02-180: FS | CHI11-04-02-180
CHI11-04-02-220 | C04/02-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-04-11 | 2025-04-17 | 41 | CHI11-04-02-205: FF 2 | CHI11-04-02-205
CHI11-04-02-225 | C04/02-DH- Set PDUs | 4 | 4 | 2025-04-11 | 2025-04-16 | 49 | CHI11-04-02-180: FS | CHI11-04-02-180
CHI11-04-02-250 | C04/02-DH- Raise HACs | 4 | 4 | 2025-04-18 | 2025-04-22 | 41 | CHI11-04-02-215: FS, CHI11-04-02-220: FS | CHI11-04-02-215, CHI11-04-02-220
CHI11-04-02-260 | C04/02-DH- Detail HACs | 4 | 4 | 2025-04-23 | 2025-04-26 | 56 | CHI11-04-02-250: FS | CHI11-04-02-250
CHI11-04-02-265 | C04/02-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-04-23 | 2025-04-25 | 41 | CHI11-04-02-250: FS | CHI11-04-02-250
CHI11-04-02-275 | C04/02-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-04-26 | 2025-04-29 | 41 | CHI11-04-02-225: FS, CHI11-04-02-265: FS | CHI11-04-02-225, CHI11-04-02-265
CHI11-04-02-285 | C04/02-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-04-30 | 2025-05-06 | 41 | CHI11-04-02-275: FS | CHI11-04-02-275
CHI11-04-02-310 | C04/02-DH- Terminate PDUs | 3 | 3 | 2025-05-28 | 2025-05-30 | 25 | CHI11-04-02-285: FS, CHI11-04-02-305: FS | CHI11-04-02-285, CHI11-04-02-305
COLO 4 - CELL 2 Electrical Room |  | 63 | 63 | 2025-03-10 | 2025-05-27 | 0
CHI11-04-02-25 | C04/02-Elec Rm- Install Framing | 2 | 2 | 2025-03-10 | 2025-03-11 | 26 | CHI11-04-02-15: FS | CHI11-04-02-15
CHI11-04-02-30 | C04/02-Elec Rm- In-Wall R/I | 2 | 2 | 2025-03-12 | 2025-03-13 | 26 | CHI11-04-02-25: FS | CHI11-04-02-25
CHI11-04-02-45 | C04/02-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-03-14 | 2025-03-15 | 28 | CHI11-04-02-30: FS | CHI11-04-02-30
CHI11-04-02-50 | C04/02-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-03-14 | 2025-03-18 | 26 | CHI11-04-02-30: FS | CHI11-04-02-30
CHI11-04-02-70 | C04/02-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-03-17 | 2025-03-18 | 28 | CHI11-04-02-45: FS | CHI11-04-02-45
CHI11-04-02-75 | C04/02-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-03-17 | 2025-03-19 | 28 | CHI11-04-02-70: SS | CHI11-04-02-70
CHI11-04-02-95 | C04/02-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-03-19 | 2025-03-20 | 26 | CHI11-04-02-50: FS | CHI11-04-02-50
CHI11-04-02-100 | C04/02-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-19 | 2025-03-19 | 28 | CHI11-04-02-75: FF | CHI11-04-02-75
CHI11-04-02-120 | C04/02-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-03-20 | 2025-03-21 | 28 | CHI11-04-02-100: FS | CHI11-04-02-100
CHI11-04-02-125 | C04/02-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-03-21 | 2025-03-24 | 26 | CHI11-04-02-95: FS | CHI11-04-02-95
CHI11-04-02-140 | C04/02-Elec Rm- General Cleaning | 1 | 1 | 2025-03-25 | 2025-03-25 | 26 | CHI11-04-02-125: FS | CHI11-04-02-125
CHI11-04-02-145 | C04/02-Elec Rm- Set Electrical Equipments | 4 | 4 | 2025-03-26 | 2025-03-29 | 26 | CHI11-04-02-140: FS, CHI11-04-02-120: FS | CHI11-04-02-140, CHI11-04-02-120
CHI11-04-02-290 | C04/02-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | 11 | 11 | 2025-05-01 | 2025-05-14 | 0 | CHI11-04-01-290: FS, CHI11-04-02-145: FS | CHI11-04-01-290, CHI11-04-02-145
CHI11-04-02-300 | C04/02-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-05-15 | 2025-05-19 | 0 | CHI11-04-02-290: FS | CHI11-04-02-290
CHI11-04-02-305 | C04/02-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | 9 | 9 | 2025-05-15 | 2025-05-27 | 0 | CHI11-04-02-290: FS, CHI11-04-02-300: SS | CHI11-04-02-290, CHI11-04-02-300
COLO 4 - CELL 2 Mechanical Gallery |  | 44 | 44 | 2025-03-17 | 2025-05-09 | 41
CHI11-04-02-80 | C04/02-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-03-17 | 2025-03-18 | 41 | CHI11-04-02-45: FS, CHI11-04-02-35: FS | CHI11-04-02-45, CHI11-04-02-35
CHI11-04-02-105 | C04/02-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-03-19 | 2025-03-20 | 41 | CHI11-04-02-80: FS | CHI11-04-02-80
CHI11-04-02-110 | C04/02-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-03-19 | 2025-03-21 | 41 | CHI11-04-02-105: SS | CHI11-04-02-105
CHI11-04-02-130 | C04/02-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-03-24 | 2025-03-29 | 41 | CHI11-04-02-110: FS | CHI11-04-02-110
CHI11-04-02-160 | C04/02-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-03-31 | 2025-04-05 | 41 | CHI11-04-02-130: FS | CHI11-04-02-130
CHI11-04-02-175 | C04/02-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-04-04 | 2025-04-05 | 41 | CHI11-04-02-160: FF, CHI11-04-02-20: FS | CHI11-04-02-160, CHI11-04-02-20
CHI11-04-02-190 | C04/02-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-04-07 | 2025-04-08 | 41 | CHI11-04-02-175: FS | CHI11-04-02-175
CHI11-04-02-195 | C04/02-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-04-07 | 2025-04-07 | 41 | CHI11-04-02-160: FS, CHI11-04-02-110: FF | CHI11-04-02-160, CHI11-04-02-110
CHI11-04-02-200 | C04/02-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-04-08 | 2025-04-11 | 41 | CHI11-04-02-195: FS | CHI11-04-02-195
CHI11-04-02-210 | C04/02-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-04-09 | 2025-04-10 | 41 | CHI11-04-02-190: FS | CHI11-04-02-190
CHI11-04-02-230 | C04/02-Mech Gallery- General Cleaning | 3 | 3 | 2025-04-11 | 2025-04-15 | 41 | CHI11-04-02-210: FS | CHI11-04-02-210
CHI11-04-02-235 | C04/02-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-04-14 | 2025-04-15 | 41 | CHI11-04-02-200: FS, CHI11-04-02-195: FS | CHI11-04-02-200, CHI11-04-02-195
CHI11-04-02-240 | C04/02-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-04-14 | 2025-04-24 | 45 | CHI11-04-02-200: FS | CHI11-04-02-200
CHI11-04-02-245 | C04/02-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-04-16 | 2025-04-19 | 41 | CHI11-04-02-230: FS, CHI11-04-02-235: FS | CHI11-04-02-230, CHI11-04-02-235
CHI11-04-02-255 | C04/02-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-04-21 | 2025-05-05 | 41 | CHI11-04-02-245: FS | CHI11-04-02-245
CHI11-04-02-270 | C04/02-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-04-25 | 2025-05-05 | 45 | CHI11-04-02-240: FS | CHI11-04-02-240
CHI11-04-02-295 | C04/02-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-05-06 | 2025-05-09 | 41 | CHI11-04-02-255: FS | CHI11-04-02-255
COLO 4 - CELL 2 Punchlist |  | 10 | 10 | 2025-05-31 | 2025-06-11 | 30
CHI11-04-02-280 | C04/02- Punchlist | 10 | 10 | 2025-05-31 | 2025-06-11 | 30 | CHI11-04-02-295: FS, CHI11-04-02-305: FS, CHI11-04-02-310: FS, CHI11-04-02-215: FS, CHI11-04-02-260: FS | CHI11-04-02-295, CHI11-04-02-305, CHI11-04-02-310, CHI11-04-02-215, CHI11-04-02-260
COLO 4 - CELL 3 |  | 102 | 102 | 2025-03-28 | 2025-08-02 | 5
COLO 4 - CELL 3 Data Hall |  | 92 | 92 | 2025-03-28 | 2025-07-21 | 5
CHI11-04-03-10 | C04/03-DH- Layout Framing | 1 | 1 | 2025-03-28 | 2025-03-28 | 0 | CHI11-04-04-40: FS | CHI11-04-04-40
CHI11-04-03-15 | C04/03-DH- Install Framing | 3 | 3 | 2025-03-29 | 2025-04-01 | 0 | CHI11-04-03-10: FS | CHI11-04-03-10
CHI11-04-03-20 | C04/03-DH- In-Wall R/I | 3 | 3 | 2025-04-02 | 2025-04-04 | 39 | CHI11-04-03-15: FS | CHI11-04-03-15
CHI11-04-03-35 | C04/03-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-04-05 | 2025-04-08 | 39 | CHI11-04-03-20: FS | CHI11-04-03-20
CHI11-04-03-40 | C04/03-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-04-05 | 2025-04-08 | 39 | CHI11-04-03-20: FS | CHI11-04-03-20
CHI11-04-03-55 | C04/03-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-04-09 | 2025-04-11 | 44 | CHI11-04-03-35: FS | CHI11-04-03-35
CHI11-04-03-60 | C04/03-DH- Overhead R/I - Electrical | 4 | 4 | 2025-04-09 | 2025-04-14 | 44 | CHI11-04-03-55: SS | CHI11-04-03-55
CHI11-04-03-65 | C04/03-DH- Finish Dry-Wall | 3 | 3 | 2025-04-09 | 2025-04-11 | 39 | CHI11-04-03-40: FS | CHI11-04-03-40
CHI11-04-03-85 | C04/03-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-04-11 | 2025-04-14 | 44 | CHI11-04-03-60: FF | CHI11-04-03-60
CHI11-04-03-90 | C04/03-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-04-11 | 2025-04-14 | 44 | CHI11-04-03-85: FF, CHI11-04-03-60: FF | CHI11-04-03-85, CHI11-04-03-60
CHI11-04-03-115 | C04/03-DH- Paint Dry-Wall | 3 | 3 | 2025-04-14 | 2025-04-16 | 39 | CHI11-04-03-65: FS | CHI11-04-03-65
CHI11-04-03-135 | C04/03-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-04-17 | 2025-04-19 | 39 | CHI11-04-03-115: FS | CHI11-04-03-115
CHI11-04-03-150 | C04/03-DH- Install Secondary Steel | 2 | 2 | 2025-04-21 | 2025-04-22 | 39 | CHI11-04-03-90: FS, CHI11-04-03-135: FS | CHI11-04-03-90, CHI11-04-03-135
CHI11-04-03-155 | C04/03-DH- Paint Secondary Steel | 2 | 2 | 2025-04-23 | 2025-04-24 | 39 | CHI11-04-03-150: FS | CHI11-04-03-150
CHI11-04-03-165 | C04/03-DH- General Cleaning | 1 | 1 | 2025-04-25 | 2025-04-25 | 42 | CHI11-04-03-155: FS | CHI11-04-03-155
CHI11-04-03-170 | C04/03-DH- Install Ceiling Grid | 4 | 4 | 2025-04-25 | 2025-04-29 | 39 | CHI11-04-03-85: FS, CHI11-04-03-90: FS, CHI11-04-03-155: FS | CHI11-04-03-85, CHI11-04-03-90, CHI11-04-03-155
CHI11-04-03-180 | C04/03-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-04-30 | 2025-05-05 | 42 | CHI11-04-03-170: FS | CHI11-04-03-170
CHI11-04-03-185 | C04/03-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-04-30 | 2025-05-06 | 39 | CHI11-04-03-170: FS, CHI11-04-03-165: FS | CHI11-04-03-170, CHI11-04-03-165
CHI11-04-03-205 | C04/03-DH- Install Busways on HAC Arms | 5 | 5 | 2025-05-02 | 2025-05-08 | 39 | CHI11-04-03-185: FF 2 | CHI11-04-03-185
CHI11-04-03-215 | C04/03-DH- Install Device Tiles | 2 | 2 | 2025-05-06 | 2025-05-07 | 42 | CHI11-04-03-180: FS | CHI11-04-03-180
CHI11-04-03-220 | C04/03-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-05-06 | 2025-05-10 | 39 | CHI11-04-03-205: FF 2 | CHI11-04-03-205
CHI11-04-03-225 | C04/03-DH- Set PDUs | 4 | 4 | 2025-05-06 | 2025-05-09 | 47 | CHI11-04-03-180: FS | CHI11-04-03-180
CHI11-04-03-250 | C04/03-DH- Raise HACs | 4 | 4 | 2025-05-12 | 2025-05-15 | 39 | CHI11-04-03-215: FS, CHI11-04-03-220: FS | CHI11-04-03-215, CHI11-04-03-220
CHI11-04-03-260 | C04/03-DH- Detail HACs | 4 | 4 | 2025-05-16 | 2025-05-20 | 53 | CHI11-04-03-250: FS | CHI11-04-03-250
CHI11-04-03-265 | C04/03-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-05-16 | 2025-05-19 | 39 | CHI11-04-03-250: FS | CHI11-04-03-250
CHI11-04-03-275 | C04/03-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-05-20 | 2025-05-22 | 39 | CHI11-04-03-225: FS, CHI11-04-03-265: FS | CHI11-04-03-225, CHI11-04-03-265
CHI11-04-03-285 | C04/03-DH- Pull Feeders from PDUs to Busways | 4 | 4 | 2025-05-23 | 2025-05-29 | 39 | CHI11-04-03-275: FS | CHI11-04-03-275
CHI11-04-03-310 | C04/03-DH- Terminate PDUs | 3 | 3 | 2025-07-18 | 2025-07-21 | 0 | CHI11-04-03-285: FS, CHI11-04-03-305: FF 1 | CHI11-04-03-285, CHI11-04-03-305
COLO 4 - CELL 3 Electrical Room |  | 87 | 87 | 2025-04-02 | 2025-07-19 | 0
CHI11-04-03-25 | C04/03-Elec Rm- Install Framing | 2 | 2 | 2025-04-02 | 2025-04-03 | 39 | CHI11-04-03-15: FS | CHI11-04-03-15
CHI11-04-03-30 | C04/03-Elec Rm- In-Wall R/I | 2 | 2 | 2025-04-04 | 2025-04-05 | 39 | CHI11-04-03-25: FS | CHI11-04-03-25
CHI11-04-03-45 | C04/03-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-04-07 | 2025-04-08 | 39 | CHI11-04-03-30: FS | CHI11-04-03-30
CHI11-04-03-50 | C04/03-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-04-07 | 2025-04-10 | 49 | CHI11-04-03-30: FS | CHI11-04-03-30
CHI11-04-03-70 | C04/03-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-04-09 | 2025-04-10 | 51 | CHI11-04-03-45: FS | CHI11-04-03-45
CHI11-04-03-75 | C04/03-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-04-09 | 2025-04-11 | 51 | CHI11-04-03-70: SS | CHI11-04-03-70
CHI11-04-03-95 | C04/03-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-04-11 | 2025-04-14 | 49 | CHI11-04-03-50: FS | CHI11-04-03-50
CHI11-04-03-100 | C04/03-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-04-11 | 2025-04-11 | 51 | CHI11-04-03-75: FF | CHI11-04-03-75
CHI11-04-03-120 | C04/03-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-04-14 | 2025-04-15 | 51 | CHI11-04-03-100: FS | CHI11-04-03-100
CHI11-04-03-125 | C04/03-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-04-15 | 2025-04-16 | 49 | CHI11-04-03-95: FS | CHI11-04-03-95
CHI11-04-03-140 | C04/03-Elec Rm- General Cleaning | 1 | 1 | 2025-04-17 | 2025-04-17 | 49 | CHI11-04-03-125: FS | CHI11-04-03-125
CHI11-04-03-145 | C04/03-Elec Rm- Set Electrical Equipments | 4 | 4 | 2025-04-18 | 2025-04-22 | 49 | CHI11-04-03-140: FS, CHI11-04-03-120: FS | CHI11-04-03-140, CHI11-04-03-120
CHI11-04-03-295 | C04/03-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | 11 | 11 | 2025-06-24 | 2025-07-08 | 0 | CHI11-04-04-305: FS, CHI11-04-03-145: FS | CHI11-04-04-305, CHI11-04-03-145
CHI11-04-03-300 | C04/03-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-07-09 | 2025-07-12 | 0 | CHI11-04-03-295: FS | CHI11-04-03-295
CHI11-04-03-305 | C04/03-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | 10 | 10 | 2025-07-09 | 2025-07-19 | 0 | CHI11-04-03-295: FS, CHI11-04-03-300: SS | CHI11-04-03-295, CHI11-04-03-300
COLO 4 - CELL 3 Mechanical Gallery |  | 43 | 43 | 2025-04-09 | 2025-06-02 | 39
CHI11-04-03-80 | C04/03-Mech Gallery- - Overhead R/I - Fire Protection | 2 | 2 | 2025-04-09 | 2025-04-10 | 39 | CHI11-04-03-45: FS, CHI11-04-03-35: FS | CHI11-04-03-45, CHI11-04-03-35
CHI11-04-03-105 | C04/03-Mech Gallery- - Overhead R/I - Fire Alarm | 2 | 2 | 2025-04-11 | 2025-04-14 | 39 | CHI11-04-03-80: FS | CHI11-04-03-80
CHI11-04-03-110 | C04/03-Mech Gallery- - Overhead R/I - Electrical | 3 | 3 | 2025-04-11 | 2025-04-15 | 39 | CHI11-04-03-105: SS | CHI11-04-03-105
CHI11-04-03-130 | C04/03-Mech Gallery- - Overhead R/I - Mechanical | 6 | 6 | 2025-04-16 | 2025-04-22 | 39 | CHI11-04-03-110: FS | CHI11-04-03-110
CHI11-04-03-160 | C04/03-Mech Gallery- - Overhead R/I - Plumbing | 6 | 6 | 2025-04-23 | 2025-04-29 | 39 | CHI11-04-03-130: FS | CHI11-04-03-130
CHI11-04-03-175 | C04/03-Mech Gallery- - Install Drywall [Mech Gallery] | 2 | 2 | 2025-04-28 | 2025-04-29 | 39 | CHI11-04-03-160: FF, CHI11-04-03-20: FS | CHI11-04-03-160, CHI11-04-03-20
CHI11-04-03-190 | C04/03-Mech Gallery- - Finish Dry-Wall | 2 | 2 | 2025-04-30 | 2025-05-01 | 39 | CHI11-04-03-175: FS | CHI11-04-03-175
CHI11-04-03-195 | C04/03-Mech Gallery- - Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-04-30 | 2025-04-30 | 39 | CHI11-04-03-160: FS, CHI11-04-03-110: FF | CHI11-04-03-160, CHI11-04-03-110
CHI11-04-03-200 | C04/03-Mech Gallery- - Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-05-01 | 2025-05-06 | 39 | CHI11-04-03-195: FS | CHI11-04-03-195
CHI11-04-03-210 | C04/03-Mech Gallery- - Paint Dry-Wall | 2 | 2 | 2025-05-02 | 2025-05-05 | 39 | CHI11-04-03-190: FS | CHI11-04-03-190
CHI11-04-03-230 | C04/03-Mech Gallery- - General Cleaning | 3 | 3 | 2025-05-06 | 2025-05-08 | 39 | CHI11-04-03-210: FS | CHI11-04-03-210
CHI11-04-03-235 | C04/03-Mech Gallery- - Install Cable Trays / Pathways | 2 | 2 | 2025-05-07 | 2025-05-08 | 39 | CHI11-04-03-200: FS, CHI11-04-03-195: FS | CHI11-04-03-200, CHI11-04-03-195
CHI11-04-03-240 | C04/03-Mech Gallery- - Install BAS Equipments | 10 | 10 | 2025-05-07 | 2025-05-17 | 43 | CHI11-04-03-200: FS | CHI11-04-03-200
CHI11-04-03-245 | C04/03-Mech Gallery- - Set Mechanical Equipments | 4 | 4 | 2025-05-09 | 2025-05-13 | 39 | CHI11-04-03-230: FS, CHI11-04-03-235: FS | CHI11-04-03-230, CHI11-04-03-235
CHI11-04-03-255 | C04/03-Mech Gallery- - Pull Cable to Mechanical Equipments [From Electrical Room] | 11 | 11 | 2025-05-14 | 2025-05-28 | 39 | CHI11-04-03-245: FS | CHI11-04-03-245
CHI11-04-03-270 | C04/03-Mech Gallery- - Pull & Terminate BAS Equipments | 7 | 7 | 2025-05-19 | 2025-05-28 | 43 | CHI11-04-03-240: FS | CHI11-04-03-240
CHI11-04-03-290 | C04/03-Mech Gallery- - Terminate Mechanical Equipments | 4 | 4 | 2025-05-29 | 2025-06-02 | 39 | CHI11-04-03-255: FS | CHI11-04-03-255
COLO 4 - CELL 3 Punchlist |  | 10 | 10 | 2025-07-22 | 2025-08-02 | 5
CHI11-04-03-280 | C04/03- Punchlist | 10 | 10 | 2025-07-22 | 2025-08-02 | 5 | CHI11-04-03-290: FS, CHI11-04-03-305: FS, CHI11-04-03-310: FS, CHI11-04-03-215: FS, CHI11-04-03-260: FS | CHI11-04-03-290, CHI11-04-03-305, CHI11-04-03-310, CHI11-04-03-215, CHI11-04-03-260
COLO 4 - CELL 4 |  | 93 | 93 | 2025-03-15 | 2025-07-10 | 16
COLO 4 - CELL 4 Data Hall |  | 83 | 83 | 2025-03-15 | 2025-06-26 | 16
CHI11-04-04-10 | C04/04-DH-Layout Framing | 1 | 1 | 2025-03-15 | 2025-03-15 | 0 | CHI11-04-02-40: SS 2 | CHI11-04-02-40
CHI11-04-04-15 | C04/04-DH-Install Framing | 3 | 3 | 2025-03-17 | 2025-03-19 | 0 | CHI11-04-04-10: FS | CHI11-04-04-10
CHI11-04-04-20 | C04/04-DH-In-Wall R/I | 3 | 3 | 2025-03-20 | 2025-03-24 | 0 | CHI11-04-04-15: FS | CHI11-04-04-15
CHI11-04-04-35 | C04/04-DH-Overhead R/I - Fire Protection | 3 | 3 | 2025-03-25 | 2025-03-27 | 40 | CHI11-04-04-20: FS | CHI11-04-04-20
CHI11-04-04-40 | C04/04-DH-Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-03-25 | 2025-03-27 | 0 | CHI11-04-04-20: FS | CHI11-04-04-20
CHI11-04-04-55 | C04/04-DH-Overhead R/I - Fire Alarm | 3 | 3 | 2025-03-28 | 2025-03-31 | 45 | CHI11-04-04-35: FS | CHI11-04-04-35
CHI11-04-04-60 | C04/04-DH-Overhead R/I - Electrical | 4 | 4 | 2025-03-28 | 2025-04-01 | 45 | CHI11-04-04-55: SS | CHI11-04-04-55
CHI11-04-04-65 | C04/04-DH-Finish Dry-Wall | 3 | 3 | 2025-03-28 | 2025-03-31 | 40 | CHI11-04-04-40: FS | CHI11-04-04-40
CHI11-04-04-85 | C04/04-DH-Overhead R/I - Mechanical | 2 | 2 | 2025-03-31 | 2025-04-01 | 45 | CHI11-04-04-60: FF | CHI11-04-04-60
CHI11-04-04-90 | C04/04-DH-Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-03-31 | 2025-04-01 | 45 | CHI11-04-04-85: FF, CHI11-04-04-60: FF | CHI11-04-04-85, CHI11-04-04-60
CHI11-04-04-115 | C04/04-DH-Paint Dry-Wall | 3 | 3 | 2025-04-01 | 2025-04-03 | 40 | CHI11-04-04-65: FS | CHI11-04-04-65
CHI11-04-04-135 | C04/04-DH-Install Screen Mesh + Caulking | 3 | 3 | 2025-04-04 | 2025-04-07 | 40 | CHI11-04-04-115: FS | CHI11-04-04-115
CHI11-04-04-150 | C04/04-DH-Install Secondary Steel | 2 | 2 | 2025-04-08 | 2025-04-09 | 40 | CHI11-04-04-90: FS, CHI11-04-04-135: FS | CHI11-04-04-90, CHI11-04-04-135
CHI11-04-04-155 | C04/04-DH-Paint Secondary Steel | 2 | 2 | 2025-04-10 | 2025-04-11 | 40 | CHI11-04-04-150: FS | CHI11-04-04-150
CHI11-04-04-165 | C04/04-DH-General Cleaning | 1 | 1 | 2025-04-14 | 2025-04-14 | 43 | CHI11-04-04-155: FS | CHI11-04-04-155
CHI11-04-04-170 | C04/04-DH-Install Ceiling Grid | 4 | 4 | 2025-04-14 | 2025-04-17 | 40 | CHI11-04-04-85: FS, CHI11-04-04-90: FS, CHI11-04-04-155: FS | CHI11-04-04-85, CHI11-04-04-90, CHI11-04-04-155
CHI11-04-04-180 | C04/04-DH-Install Perimeter Cable Trays | 4 | 4 | 2025-04-18 | 2025-04-22 | 43 | CHI11-04-04-170: FS | CHI11-04-04-170
CHI11-04-04-185 | C04/04-DH-Assemble HACs [Qty - 5] | 5 | 5 | 2025-04-18 | 2025-04-23 | 40 | CHI11-04-04-170: FS, CHI11-04-04-165: FS | CHI11-04-04-170, CHI11-04-04-165
CHI11-04-04-205 | C04/04-DH-Install Busways on HAC Arms | 5 | 5 | 2025-04-21 | 2025-04-25 | 40 | CHI11-04-04-185: FF 2 | CHI11-04-04-185
CHI11-04-04-215 | C04/04-DH-Install Device Tiles | 2 | 2 | 2025-04-23 | 2025-04-24 | 43 | CHI11-04-04-180: FS | CHI11-04-04-180
CHI11-04-04-220 | C04/04-DH-Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-04-23 | 2025-04-28 | 40 | CHI11-04-04-205: FF 2 | CHI11-04-04-205
CHI11-04-04-225 | C04/04-DH-Set PDUs | 4 | 4 | 2025-04-23 | 2025-04-26 | 48 | CHI11-04-04-180: FS | CHI11-04-04-180
CHI11-04-04-250 | C04/04-DH-Raise HACs | 4 | 4 | 2025-04-29 | 2025-05-02 | 40 | CHI11-04-04-215: FS, CHI11-04-04-220: FS | CHI11-04-04-215, CHI11-04-04-220
CHI11-04-04-260 | C04/04-DH-Detail HACs | 4 | 4 | 2025-05-05 | 2025-05-08 | 55 | CHI11-04-04-250: FS | CHI11-04-04-250
CHI11-04-04-265 | C04/04-DH-Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-05-05 | 2025-05-07 | 40 | CHI11-04-04-250: FS | CHI11-04-04-250
CHI11-04-04-275 | C04/04-DH-Install Conduits PDU to Cable Trays | 3 | 3 | 2025-05-08 | 2025-05-10 | 40 | CHI11-04-04-225: FS, CHI11-04-04-265: FS | CHI11-04-04-225, CHI11-04-04-265
CHI11-04-04-285 | C04/04-DH-Pull Feeders from PDUs to Busways | 5 | 5 | 2025-05-12 | 2025-05-16 | 40 | CHI11-04-04-275: FS | CHI11-04-04-275
CHI11-04-04-310 | C04/04-DH-Terminate PDUs | 3 | 3 | 2025-06-24 | 2025-06-26 | 11 | CHI11-04-04-285: FS, CHI11-04-04-305: FS | CHI11-04-04-285, CHI11-04-04-305
COLO 4 - CELL 4 Electrical Room |  | 76 | 76 | 2025-03-20 | 2025-06-23 | 0
CHI11-04-04-25 | C04/04-Elec Rm-Install Framing | 2 | 2 | 2025-03-20 | 2025-03-21 | 37 | CHI11-04-04-15: FS | CHI11-04-04-15
CHI11-04-04-30 | C04/04-Elec Rm-In-Wall R/I | 2 | 2 | 2025-03-24 | 2025-03-25 | 37 | CHI11-04-04-25: FS | CHI11-04-04-25
CHI11-04-04-45 | C04/04-Elec Rm-Overhead R/I - Fire Protection | 2 | 2 | 2025-03-26 | 2025-03-27 | 39 | CHI11-04-04-30: FS | CHI11-04-04-30
CHI11-04-04-50 | C04/04-Elec Rm-Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-03-26 | 2025-03-29 | 37 | CHI11-04-04-30: FS | CHI11-04-04-30
CHI11-04-04-70 | C04/04-Elec Rm-Overhead R/I - Fire Alarm | 2 | 2 | 2025-03-28 | 2025-03-29 | 39 | CHI11-04-04-45: FS | CHI11-04-04-45
CHI11-04-04-75 | C04/04-Elec Rm-Overhead R/I - Electrical | 3 | 3 | 2025-03-28 | 2025-03-31 | 39 | CHI11-04-04-70: SS | CHI11-04-04-70
CHI11-04-04-95 | C04/04-Elec Rm-Finish Dry-Wall | 2 | 2 | 2025-03-31 | 2025-04-01 | 37 | CHI11-04-04-50: FS | CHI11-04-04-50
CHI11-04-04-100 | C04/04-Elec Rm-Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-03-31 | 2025-03-31 | 39 | CHI11-04-04-75: FF | CHI11-04-04-75
CHI11-04-04-120 | C04/04-Elec Rm-Install Cable Trays / Pathways | 2 | 2 | 2025-04-01 | 2025-04-02 | 39 | CHI11-04-04-100: FS | CHI11-04-04-100
CHI11-04-04-125 | C04/04-Elec Rm-Paint Dry-Wall | 2 | 2 | 2025-04-02 | 2025-04-03 | 37 | CHI11-04-04-95: FS | CHI11-04-04-95
CHI11-04-04-140 | C04/04-Elec Rm-General Cleaning | 1 | 1 | 2025-04-04 | 2025-04-04 | 37 | CHI11-04-04-125: FS | CHI11-04-04-125
CHI11-04-04-145 | C04/04-Elec Rm-Set Electrical Equipments | 4 | 4 | 2025-04-05 | 2025-04-09 | 37 | CHI11-04-04-140: FS, CHI11-04-04-120: FS | CHI11-04-04-140, CHI11-04-04-120
CHI11-04-04-295 | C04/04-Elec Rm-Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | 11 | 11 | 2025-05-28 | 2025-06-09 | 0 | CHI11-04-02-305: FS, CHI11-04-04-145: FS | CHI11-04-02-305, CHI11-04-04-145
CHI11-04-04-300 | C04/04-Elec Rm-Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-06-10 | 2025-06-13 | 0 | CHI11-04-04-295: FS | CHI11-04-04-295
CHI11-04-04-305 | C04/04-Elec Rm-Pull Feeders from Electrical Room to PDUs Pull Crew 2 | 11 | 11 | 2025-06-10 | 2025-06-23 | 0 | CHI11-04-04-295: FS, CHI11-04-04-300: SS | CHI11-04-04-295, CHI11-04-04-300
COLO 4 - CELL 4 Mechanical Gallery |  | 44 | 44 | 2025-03-28 | 2025-05-20 | 40
CHI11-04-04-80 | C04/04-Mech Gallery-Overhead R/I - Fire Protection | 2 | 2 | 2025-03-28 | 2025-03-29 | 40 | CHI11-04-04-45: FS, CHI11-04-04-35: FS | CHI11-04-04-45, CHI11-04-04-35
CHI11-04-04-105 | C04/04-Mech Gallery-Overhead R/I - Fire Alarm | 2 | 2 | 2025-03-31 | 2025-04-01 | 40 | CHI11-04-04-80: FS | CHI11-04-04-80
CHI11-04-04-110 | C04/04-Mech Gallery-Overhead R/I - Electrical | 3 | 3 | 2025-03-31 | 2025-04-02 | 40 | CHI11-04-04-105: SS | CHI11-04-04-105
CHI11-04-04-130 | C04/04-Mech Gallery-Overhead R/I - Mechanical | 6 | 6 | 2025-04-03 | 2025-04-09 | 40 | CHI11-04-04-110: FS | CHI11-04-04-110
CHI11-04-04-160 | C04/04-Mech Gallery-Overhead R/I - Plumbing | 6 | 6 | 2025-04-10 | 2025-04-17 | 40 | CHI11-04-04-130: FS | CHI11-04-04-130
CHI11-04-04-175 | C04/04-Mech Gallery-Install Drywall [Mech Gallery] | 2 | 2 | 2025-04-16 | 2025-04-17 | 40 | CHI11-04-04-160: FF, CHI11-04-04-20: FS | CHI11-04-04-160, CHI11-04-04-20
CHI11-04-04-190 | C04/04-Mech Gallery-Finish Dry-Wall | 2 | 2 | 2025-04-18 | 2025-04-19 | 40 | CHI11-04-04-175: FS | CHI11-04-04-175
CHI11-04-04-195 | C04/04-Mech Gallery-Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-04-18 | 2025-04-18 | 40 | CHI11-04-04-160: FS, CHI11-04-04-110: FF | CHI11-04-04-160, CHI11-04-04-110
CHI11-04-04-200 | C04/04-Mech Gallery-Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-04-19 | 2025-04-23 | 40 | CHI11-04-04-195: FS | CHI11-04-04-195
CHI11-04-04-210 | C04/04-Mech Gallery-Paint Dry-Wall | 2 | 2 | 2025-04-21 | 2025-04-22 | 40 | CHI11-04-04-190: FS | CHI11-04-04-190
CHI11-04-04-230 | C04/04-Mech Gallery-General Cleaning | 3 | 3 | 2025-04-23 | 2025-04-25 | 40 | CHI11-04-04-210: FS | CHI11-04-04-210
CHI11-04-04-235 | C04/04-Mech Gallery-Install Cable Trays / Pathways | 2 | 2 | 2025-04-24 | 2025-04-25 | 40 | CHI11-04-04-200: FS, CHI11-04-04-195: FS | CHI11-04-04-200, CHI11-04-04-195
CHI11-04-04-240 | C04/04-Mech Gallery-Install BAS Equipments | 10 | 10 | 2025-04-24 | 2025-05-06 | 44 | CHI11-04-04-200: FS | CHI11-04-04-200
CHI11-04-04-245 | C04/04-Mech Gallery-Set Mechanical Equipments | 4 | 4 | 2025-04-26 | 2025-04-30 | 40 | CHI11-04-04-230: FS, CHI11-04-04-235: FS | CHI11-04-04-230, CHI11-04-04-235
CHI11-04-04-255 | C04/04-Mech Gallery-Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-05-01 | 2025-05-15 | 40 | CHI11-04-04-245: FS | CHI11-04-04-245
CHI11-04-04-270 | C04/04-Mech Gallery-Pull & Terminate BAS Equipments | 8 | 8 | 2025-05-07 | 2025-05-15 | 44 | CHI11-04-04-240: FS | CHI11-04-04-240
CHI11-04-04-290 | C04/04-Mech Gallery-Terminate Mechanical Equipments | 4 | 4 | 2025-05-16 | 2025-05-20 | 40 | CHI11-04-04-255: FS | CHI11-04-04-255
COLO 4 - CELL 4 Punchlist |  | 10 | 10 | 2025-06-27 | 2025-07-10 | 16
CHI11-04-04-280 | C04/04- Punchlist | 10 | 10 | 2025-06-27 | 2025-07-10 | 16 | CHI11-04-04-290: FS, CHI11-04-04-305: FS, CHI11-04-04-310: FS, CHI11-04-04-215: FS, CHI11-04-04-260: FS | CHI11-04-04-290, CHI11-04-04-305, CHI11-04-04-310, CHI11-04-04-215, CHI11-04-04-260
COLO 5 |  | 115 | 115 | 2025-03-31 | 2025-08-21 | 5
COLO 5 - CELL 1 |  | 63 | 63 | 2025-03-31 | 2025-06-17 | 28
COLO 5 - CELL 1 Data Hall |  | 53 | 53 | 2025-03-31 | 2025-06-04 | 28
CHI11-05-01-10 | C05/01-DH- Layout Framing | 1 | 1 | 2025-03-31 | 2025-03-31 | 0 | CHI11-04-03-15: SS 1, CHI11-05-C&S-30: FS, CHI-11-05-DRY-F: FS | CHI11-04-03-15, CHI11-05-C&S-30, CHI-11-05-DRY-F
CHI11-05-01-15 | C05/01-DH- Install Framing | 3 | 3 | 2025-04-01 | 2025-04-03 | 0 | CHI11-05-01-10: FS | CHI11-05-01-10
CHI11-05-01-20 | C05/01-DH- In-Wall R/I | 3 | 3 | 2025-04-04 | 2025-04-07 | 20 | CHI11-05-01-15: FS | CHI11-05-01-15
CHI11-05-01-35 | C05/01-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-04-08 | 2025-04-10 | 22 | CHI11-05-01-20: FS | CHI11-05-01-20
CHI11-05-01-40 | C05/01-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-04-08 | 2025-04-10 | 20 | CHI11-05-01-20: FS | CHI11-05-01-20
CHI11-05-01-55 | C05/01-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-04-11 | 2025-04-15 | 28 | CHI11-05-01-35: FS | CHI11-05-01-35
CHI11-05-01-60 | C05/01-DH- Overhead R/I - Electrical | 4 | 4 | 2025-04-11 | 2025-04-16 | 28 | CHI11-05-01-55: SS | CHI11-05-01-55
CHI11-05-01-65 | C05/01-DH- Finish Dry-Wall | 3 | 3 | 2025-04-11 | 2025-04-15 | 23 | CHI11-05-01-40: FS | CHI11-05-01-40
CHI11-05-01-85 | C05/01-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-04-15 | 2025-04-16 | 28 | CHI11-05-01-60: FF | CHI11-05-01-60
CHI11-05-01-90 | C05/01-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-04-15 | 2025-04-16 | 28 | CHI11-05-01-85: FF, CHI11-05-01-60: FF | CHI11-05-01-85, CHI11-05-01-60
CHI11-05-01-115 | C05/01-DH- Paint Dry-Wall | 3 | 3 | 2025-04-16 | 2025-04-18 | 23 | CHI11-05-01-65: FS | CHI11-05-01-65
CHI11-05-01-135 | C05/01-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-04-19 | 2025-04-22 | 23 | CHI11-05-01-115: FS | CHI11-05-01-115
CHI11-05-01-150 | C05/01-DH- Install Secondary Steel | 2 | 2 | 2025-04-23 | 2025-04-24 | 23 | CHI11-05-01-90: FS, CHI11-05-01-135: FS | CHI11-05-01-90, CHI11-05-01-135
CHI11-05-01-155 | C05/01-DH- Paint Secondary Steel | 2 | 2 | 2025-04-25 | 2025-04-26 | 23 | CHI11-05-01-150: FS | CHI11-05-01-150
CHI11-05-01-165 | C05/01-DH- General Cleaning | 1 | 1 | 2025-04-28 | 2025-04-28 | 24 | CHI11-05-01-155: FS | CHI11-05-01-155
CHI11-05-01-170 | C05/01-DH- Install Ceiling Grid | 4 | 4 | 2025-04-28 | 2025-05-01 | 23 | CHI11-05-01-85: FS, CHI11-05-01-90: FS, CHI11-05-01-155: FS | CHI11-05-01-85, CHI11-05-01-90, CHI11-05-01-155
CHI11-05-01-180 | C05/01-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-05-02 | 2025-05-07 | 26 | CHI11-05-01-170: FS | CHI11-05-01-170
CHI11-05-01-185 | C05/01-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-05-02 | 2025-05-08 | 23 | CHI-11-05-HAC-03: FS, CHI11-05-01-170: FS, CHI11-05-01-165: FS | CHI-11-05-HAC-03, CHI11-05-01-170, CHI11-05-01-165
CHI11-05-01-210 | C05/01-DH- Install Busways on HAC Arms | 5 | 5 | 2025-05-06 | 2025-05-10 | 23 | CHI-11-05-BUS-03: FS, CHI11-05-01-185: FF 2 | CHI-11-05-BUS-03, CHI11-05-01-185
CHI11-05-01-220 | C05/01-DH- Install Device Tiles | 2 | 2 | 2025-05-08 | 2025-05-09 | 26 | CHI11-05-01-180: FS | CHI11-05-01-180
CHI11-05-01-225 | C05/01-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-05-08 | 2025-05-13 | 23 | CHI11-05-01-210: FF 2 | CHI11-05-01-210
CHI11-05-01-230 | C05/01-DH- Set PDUs | 4 | 4 | 2025-05-08 | 2025-05-12 | 31 | CHI-11-05-PDU-03: FS, CHI11-05-01-180: FS | CHI-11-05-PDU-03, CHI11-05-01-180
CHI11-05-01-255 | C05/01-DH- Raise HACs | 4 | 4 | 2025-05-14 | 2025-05-17 | 23 | CHI11-05-01-220: FS, CHI11-05-01-225: FS | CHI11-05-01-220, CHI11-05-01-225
CHI11-05-01-275 | C05/01-DH- Detail HACs | 4 | 4 | 2025-05-19 | 2025-05-22 | 37 | CHI11-05-01-255: FS | CHI11-05-01-255
CHI11-05-01-280 | C05/01-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-05-19 | 2025-05-21 | 23 | CHI11-05-01-255: FS | CHI11-05-01-255
CHI11-05-01-290 | C05/01-DH- Install Conduits PDU to Cable Trays | 2 | 2 | 2025-05-22 | 2025-05-23 | 23 | CHI11-05-01-230: FS, CHI11-05-01-280: FS | CHI11-05-01-230, CHI11-05-01-280
CHI11-05-01-300 | C05/01-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-05-27 | 2025-05-31 | 23 | CHI11-05-01-290: FS | CHI11-05-01-290
CHI11-05-01-310 | C05/01-DH- Terminate PDUs | 3 | 3 | 2025-06-02 | 2025-06-04 | 23 | CHI11-05-01-300: FS, CHI11-05-01-265: FS | CHI11-05-01-300, CHI11-05-01-265
COLO 5 - CELL 1 Electrical Room |  | 44 | 44 | 2025-04-04 | 2025-05-29 | 0
CHI11-05-01-25 | C05/01-Elec Rm- Install Framing | 2 | 2 | 2025-04-04 | 2025-04-05 | 0 | CHI11-05-01-15: FS | CHI11-05-01-15
CHI11-05-01-30 | C05/01-Elec Rm- In-Wall R/I | 2 | 2 | 2025-04-07 | 2025-04-08 | 0 | CHI11-05-01-25: FS | CHI11-05-01-25
CHI11-05-01-45 | C05/01-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-04-09 | 2025-04-10 | 2 | CHI11-05-01-30: FS | CHI11-05-01-30
CHI11-05-01-50 | C05/01-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-04-09 | 2025-04-14 | 0 | CHI11-05-01-30: FS | CHI11-05-01-30
CHI11-05-01-70 | C05/01-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-04-11 | 2025-04-14 | 2 | CHI11-05-01-45: FS | CHI11-05-01-45
CHI11-05-01-75 | C05/01-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-04-11 | 2025-04-15 | 2 | CHI11-05-01-70: SS | CHI11-05-01-70
CHI11-05-01-95 | C05/01-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-04-15 | 2025-04-16 | 0 | CHI11-05-01-50: FS | CHI11-05-01-50
CHI11-05-01-100 | C05/01-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-04-15 | 2025-04-15 | 2 | CHI11-05-01-75: FF | CHI11-05-01-75
CHI11-05-01-120 | C05/01-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-04-16 | 2025-04-17 | 2 | CHI11-05-01-100: FS | CHI11-05-01-100
CHI11-05-01-125 | C05/01-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-04-17 | 2025-04-18 | 0 | CHI11-05-01-95: FS | CHI11-05-01-95
CHI11-05-01-140 | C05/01-Elec Rm- General Cleaning | 1 | 1 | 2025-04-19 | 2025-04-19 | 0 | CHI11-05-01-125: FS | CHI11-05-01-125
CHI11-05-01-145 | C05/01-Elec Rm- Set Electrical Equipments | 10 | 10 | 2025-04-21 | 2025-05-01 | 0 | CHI-11-05-UPS-03: FS, CHI-11-05-MSB-03: FS, CHI-11-05-LVS-03: FS, CHI-11-05-EPMS-03: FS, CHI-11-05-ADP-03: FS, CHI-11-05-ATS-03: FS, CHI-11-05-TCP-03: FS, CHI11-05-01-140: FS, CHI11-05-01-120: FS | CHI-11-05-UPS-03, CHI-11-05-MSB-03, CHI-11-05-LVS-03, CHI-11-05-EPMS-03, CHI-11-05-ADP-03, CHI-11-05-ATS-03, CHI-11-05-TCP-03, CHI11-05-01-140, CHI11-05-01-120
CHI11-05-01-190 | C05/01-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | 11 | 11 | 2025-05-02 | 2025-05-15 | 0 | CHI11-05-01-145: FS | CHI11-05-01-145
CHI11-05-01-260 | C05/01-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-05-16 | 2025-05-20 | 0 | CHI11-05-01-190: FS | CHI11-05-01-190
CHI11-05-01-265 | C05/01-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | 10 | 10 | 2025-05-16 | 2025-05-29 | 0 | CHI11-05-01-190: FS, CHI11-05-01-260: SS | CHI11-05-01-190, CHI11-05-01-260
COLO 5 - CELL 1 Mechanical Gallery |  | 43 | 43 | 2025-04-11 | 2025-06-04 | 23
CHI11-05-01-80 | C05/01-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-04-11 | 2025-04-14 | 22 | CHI11-05-01-45: FS, CHI11-05-01-35: FS | CHI11-05-01-45, CHI11-05-01-35
CHI11-05-01-105 | C05/01-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-04-15 | 2025-04-16 | 22 | CHI11-05-01-80: FS | CHI11-05-01-80
CHI11-05-01-110 | C05/01-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-04-15 | 2025-04-17 | 22 | CHI11-05-01-105: SS | CHI11-05-01-105
CHI11-05-01-130 | C05/01-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-04-18 | 2025-04-24 | 22 | CHI11-05-01-110: FS | CHI11-05-01-110
CHI11-05-01-160 | C05/01-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-04-25 | 2025-05-01 | 22 | CHI11-05-01-130: FS | CHI11-05-01-130
CHI11-05-01-175 | C05/01-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-04-30 | 2025-05-01 | 22 | CHI11-05-01-160: FF, CHI11-05-01-20: FS | CHI11-05-01-160, CHI11-05-01-20
CHI11-05-01-195 | C05/01-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-05-02 | 2025-05-05 | 22 | CHI11-05-01-175: FS | CHI11-05-01-175
CHI11-05-01-200 | C05/01-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-05-02 | 2025-05-02 | 23 | CHI11-05-01-160: FS, CHI11-05-01-110: FF | CHI11-05-01-160, CHI11-05-01-110
CHI11-05-01-205 | C05/01-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-05-05 | 2025-05-08 | 23 | CHI11-05-01-200: FS | CHI11-05-01-200
CHI11-05-01-215 | C05/01-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-05-06 | 2025-05-07 | 22 | CHI11-05-01-195: FS | CHI11-05-01-195
CHI11-05-01-235 | C05/01-Mech Gallery- General Cleaning | 3 | 3 | 2025-05-08 | 2025-05-10 | 22 | CHI11-05-01-215: FS | CHI11-05-01-215
CHI11-05-01-240 | C05/01-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-05-09 | 2025-05-10 | 23 | CHI11-05-01-205: FS, CHI11-05-01-200: FS | CHI11-05-01-205, CHI11-05-01-200
CHI11-05-01-245 | C05/01-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-05-09 | 2025-05-20 | 27 | CHI-11-05-BAS-03: FS, CHI11-05-01-205: FS | CHI-11-05-BAS-03, CHI11-05-01-205
CHI11-05-01-250 | C05/01-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-05-12 | 2025-05-15 | 23 | CHI-11-05-AHU-03: FS, CHI-11-05-ROJ-S: SS, CHI11-05-01-235: FS, CHI11-05-01-240: FS | CHI-11-05-AHU-03, CHI-11-05-ROJ-S, CHI11-05-01-235, CHI11-05-01-240
CHI11-05-01-270 | C05/01-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 11 | 11 | 2025-05-16 | 2025-05-30 | 23 | CHI11-05-01-250: FS | CHI11-05-01-250
CHI11-05-01-285 | C05/01-Mech Gallery- Pull & Terminate BAS Equipments | 7 | 7 | 2025-05-21 | 2025-05-30 | 27 | CHI11-05-01-245: FS | CHI11-05-01-245
CHI11-05-01-305 | C05/01-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-05-31 | 2025-06-04 | 23 | CHI11-05-01-270: FS | CHI11-05-01-270
COLO 5 - CELL 1 Punchlist |  | 10 | 10 | 2025-06-05 | 2025-06-17 | 28
CHI11-05-01-295 | C05/01-Punchlist | 10 | 10 | 2025-06-05 | 2025-06-17 | 28 | CHI11-05-01-305: FS, CHI11-05-01-265: FS, CHI11-05-01-310: FS, CHI11-05-01-220: FS, CHI11-05-01-275: FS | CHI11-05-01-305, CHI11-05-01-265, CHI11-05-01-310, CHI11-05-01-220, CHI11-05-01-275
COLO 5 - CELL 2 |  | 75 | 75 | 2025-04-08 | 2025-07-11 | 22
COLO 5 - CELL 2 Data Hall |  | 65 | 65 | 2025-04-08 | 2025-06-27 | 22
CHI11-05-02-10 | C05/02-DH- Layout Framing | 1 | 1 | 2025-04-08 | 2025-04-08 | 20 | CHI11-05-01-40: SS, CHI11-05-01-15: FS | CHI11-05-01-40, CHI11-05-01-15
CHI11-05-02-15 | C05/02-DH- Install Framing | 3 | 3 | 2025-04-09 | 2025-04-11 | 20 | CHI11-05-02-10: FS | CHI11-05-02-10
CHI11-05-02-20 | C05/02-DH- In-Wall R/I | 3 | 3 | 2025-04-14 | 2025-04-16 | 22 | CHI11-05-02-15: FS | CHI11-05-02-15
CHI11-05-02-35 | C05/02-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-04-17 | 2025-04-19 | 29 | CHI11-05-02-20: FS | CHI11-05-02-20
CHI11-05-02-40 | C05/02-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-04-17 | 2025-04-19 | 22 | CHI11-05-02-20: FS | CHI11-05-02-20
CHI11-05-02-55 | C05/02-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-04-21 | 2025-04-23 | 34 | CHI11-05-02-35: FS | CHI11-05-02-35
CHI11-05-02-60 | C05/02-DH- Overhead R/I - Electrical | 4 | 4 | 2025-04-21 | 2025-04-24 | 34 | CHI11-05-02-55: SS | CHI11-05-02-55
CHI11-05-02-65 | C05/02-DH- Finish Dry-Wall | 3 | 3 | 2025-04-21 | 2025-04-23 | 29 | CHI11-05-02-40: FS | CHI11-05-02-40
CHI11-05-02-85 | C05/02-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-04-23 | 2025-04-24 | 34 | CHI11-05-02-60: FF | CHI11-05-02-60
CHI11-05-02-90 | C05/02-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-04-23 | 2025-04-24 | 34 | CHI11-05-02-85: FF, CHI11-05-02-60: FF | CHI11-05-02-85, CHI11-05-02-60
CHI11-05-02-115 | C05/02-DH- Paint Dry-Wall | 3 | 3 | 2025-04-24 | 2025-04-26 | 29 | CHI11-05-02-65: FS | CHI11-05-02-65
CHI11-05-02-135 | C05/02-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-04-28 | 2025-04-30 | 29 | CHI11-05-02-115: FS | CHI11-05-02-115
CHI11-05-02-150 | C05/02-DH- Install Secondary Steel | 2 | 2 | 2025-05-01 | 2025-05-02 | 29 | CHI11-05-02-90: FS, CHI11-05-02-135: FS | CHI11-05-02-90, CHI11-05-02-135
CHI11-05-02-155 | C05/02-DH- Paint Secondary Steel | 2 | 2 | 2025-05-05 | 2025-05-06 | 29 | CHI11-05-02-150: FS | CHI11-05-02-150
CHI11-05-02-165 | C05/02-DH- General Cleaning | 1 | 1 | 2025-05-07 | 2025-05-07 | 32 | CHI11-05-02-155: FS | CHI11-05-02-155
CHI11-05-02-170 | C05/02-DH- Install Ceiling Grid | 4 | 4 | 2025-05-07 | 2025-05-10 | 29 | CHI11-05-02-85: FS, CHI11-05-02-90: FS, CHI11-05-02-155: FS | CHI11-05-02-85, CHI11-05-02-90, CHI11-05-02-155
CHI11-05-02-180 | C05/02-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-05-12 | 2025-05-15 | 32 | CHI11-05-02-170: FS | CHI11-05-02-170
CHI11-05-02-185 | C05/02-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-05-12 | 2025-05-16 | 29 | CHI11-05-02-170: FS, CHI11-05-02-165: FS | CHI11-05-02-170, CHI11-05-02-165
CHI11-05-02-205 | C05/02-DH- Install Busways on HAC Arms | 5 | 5 | 2025-05-14 | 2025-05-19 | 29 | CHI11-05-02-185: FF 2 | CHI11-05-02-185
CHI11-05-02-215 | C05/02-DH- Install Device Tiles | 2 | 2 | 2025-05-16 | 2025-05-17 | 32 | CHI11-05-02-180: FS | CHI11-05-02-180
CHI11-05-02-220 | C05/02-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-05-16 | 2025-05-21 | 29 | CHI11-05-02-205: FF 2 | CHI11-05-02-205
CHI11-05-02-225 | C05/02-DH- Set PDUs | 4 | 4 | 2025-05-16 | 2025-05-20 | 36 | CHI11-05-02-180: FS | CHI11-05-02-180
CHI11-05-02-250 | C05/02-DH- Raise HACs | 3 | 3 | 2025-05-22 | 2025-05-27 | 29 | CHI11-05-02-215: FS, CHI11-05-02-220: FS | CHI11-05-02-215, CHI11-05-02-220
CHI11-05-02-260 | C05/02-DH- Detail HACs | 4 | 4 | 2025-05-28 | 2025-05-31 | 44 | CHI11-05-02-250: FS | CHI11-05-02-250
CHI11-05-02-265 | C05/02-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-05-28 | 2025-05-30 | 29 | CHI11-05-02-250: FS | CHI11-05-02-250
CHI11-05-02-280 | C05/02-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-05-31 | 2025-06-03 | 29 | CHI11-05-02-225: FS, CHI11-05-02-265: FS | CHI11-05-02-225, CHI11-05-02-265
CHI11-05-02-290 | C05/02-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-06-04 | 2025-06-09 | 29 | CHI11-05-02-280: FS | CHI11-05-02-280
CHI11-05-02-310 | C05/02-DH- Terminate PDUs | 3 | 3 | 2025-06-25 | 2025-06-27 | 17 | CHI11-05-02-290: FS, CHI11-05-02-305: FS | CHI11-05-02-290, CHI11-05-02-305
COLO 5 - CELL 2 Electrical Room |  | 58 | 58 | 2025-04-14 | 2025-06-24 | 0
CHI11-05-02-25 | C05/02-Elec Rm- Install Framing | 2 | 2 | 2025-04-14 | 2025-04-15 | 20 | CHI11-05-02-15: FS | CHI11-05-02-15
CHI11-05-02-30 | C05/02-Elec Rm- In-Wall R/I | 2 | 2 | 2025-04-16 | 2025-04-17 | 20 | CHI11-05-02-25: FS | CHI11-05-02-25
CHI11-05-02-45 | C05/02-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-04-18 | 2025-04-19 | 22 | CHI11-05-02-30: FS | CHI11-05-02-30
CHI11-05-02-50 | C05/02-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-04-18 | 2025-04-22 | 20 | CHI11-05-02-30: FS | CHI11-05-02-30
CHI11-05-02-70 | C05/02-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-04-21 | 2025-04-22 | 22 | CHI11-05-02-45: FS | CHI11-05-02-45
CHI11-05-02-75 | C05/02-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-04-21 | 2025-04-23 | 22 | CHI11-05-02-70: SS | CHI11-05-02-70
CHI11-05-02-95 | C05/02-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-04-23 | 2025-04-24 | 20 | CHI11-05-02-50: FS | CHI11-05-02-50
CHI11-05-02-100 | C05/02-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-04-23 | 2025-04-23 | 22 | CHI11-05-02-75: FF | CHI11-05-02-75
CHI11-05-02-120 | C05/02-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-04-24 | 2025-04-25 | 22 | CHI11-05-02-100: FS | CHI11-05-02-100
CHI11-05-02-125 | C05/02-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-04-25 | 2025-04-26 | 20 | CHI11-05-02-95: FS | CHI11-05-02-95
CHI11-05-02-140 | C05/02-Elec Rm- General Cleaning | 1 | 1 | 2025-04-28 | 2025-04-28 | 20 | CHI11-05-02-125: FS | CHI11-05-02-125
CHI11-05-02-145 | C05/02-Elec Rm- Set Electrical Equipments | 4 | 4 | 2025-04-29 | 2025-05-02 | 20 | CHI11-05-02-140: FS, CHI11-05-02-120: FS | CHI11-05-02-140, CHI11-05-02-120
CHI11-05-02-270 | C05/02-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | 11 | 11 | 2025-05-30 | 2025-06-11 | 0 | CHI11-05-01-265: FS, CHI11-05-02-145: FS | CHI11-05-01-265, CHI11-05-02-145
CHI11-05-02-300 | C05/02-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-06-12 | 2025-06-17 | 0 | CHI11-05-02-270: FS | CHI11-05-02-270
CHI11-05-02-305 | C05/02-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | 10 | 10 | 2025-06-12 | 2025-06-24 | 0 | CHI11-05-02-270: FS, CHI11-05-02-300: SS | CHI11-05-02-270, CHI11-05-02-300
COLO 5 - CELL 2 Mechanical Gallery |  | 43 | 43 | 2025-04-21 | 2025-06-12 | 29
CHI11-05-02-80 | C05/02-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-04-21 | 2025-04-22 | 29 | CHI11-05-02-45: FS, CHI11-05-02-35: FS | CHI11-05-02-45, CHI11-05-02-35
CHI11-05-02-105 | C05/02-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-04-23 | 2025-04-24 | 29 | CHI11-05-02-80: FS | CHI11-05-02-80
CHI11-05-02-110 | C05/02-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-04-23 | 2025-04-25 | 29 | CHI11-05-02-105: SS | CHI11-05-02-105
CHI11-05-02-130 | C05/02-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-04-26 | 2025-05-02 | 29 | CHI11-05-02-110: FS | CHI11-05-02-110
CHI11-05-02-160 | C05/02-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-05-05 | 2025-05-10 | 29 | CHI11-05-02-130: FS | CHI11-05-02-130
CHI11-05-02-175 | C05/02-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-05-09 | 2025-05-10 | 29 | CHI11-05-02-160: FF, CHI11-05-02-20: FS | CHI11-05-02-160, CHI11-05-02-20
CHI11-05-02-190 | C05/02-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-05-12 | 2025-05-13 | 29 | CHI11-05-02-175: FS | CHI11-05-02-175
CHI11-05-02-195 | C05/02-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-05-12 | 2025-05-12 | 29 | CHI11-05-02-160: FS, CHI11-05-02-110: FF | CHI11-05-02-160, CHI11-05-02-110
CHI11-05-02-200 | C05/02-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-05-13 | 2025-05-16 | 29 | CHI11-05-02-195: FS | CHI11-05-02-195
CHI11-05-02-210 | C05/02-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-05-14 | 2025-05-15 | 29 | CHI11-05-02-190: FS | CHI11-05-02-190
CHI11-05-02-230 | C05/02-Mech Gallery- General Cleaning | 3 | 3 | 2025-05-16 | 2025-05-19 | 29 | CHI11-05-02-210: FS | CHI11-05-02-210
CHI11-05-02-235 | C05/02-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-05-17 | 2025-05-19 | 29 | CHI11-05-02-200: FS, CHI11-05-02-195: FS | CHI11-05-02-200, CHI11-05-02-195
CHI11-05-02-240 | C05/02-Mech Gallery- Install BAS Equipments | 9 | 9 | 2025-05-17 | 2025-05-29 | 33 | CHI11-05-02-200: FS | CHI11-05-02-200
CHI11-05-02-245 | C05/02-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-05-20 | 2025-05-23 | 29 | CHI11-05-02-230: FS, CHI11-05-02-235: FS | CHI11-05-02-230, CHI11-05-02-235
CHI11-05-02-255 | C05/02-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 11 | 11 | 2025-05-27 | 2025-06-07 | 29 | CHI11-05-02-245: FS | CHI11-05-02-245
CHI11-05-02-275 | C05/02-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-05-30 | 2025-06-07 | 33 | CHI11-05-02-240: FS | CHI11-05-02-240
CHI11-05-02-295 | C05/02-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-06-09 | 2025-06-12 | 29 | CHI11-05-02-255: FS | CHI11-05-02-255
COLO 5 - CELL 2 Punchlist |  | 10 | 10 | 2025-06-28 | 2025-07-11 | 22
CHI11-05-02-285 | C05/02- Punchlist | 10 | 10 | 2025-06-28 | 2025-07-11 | 22 | CHI11-05-02-295: FS, CHI11-05-02-305: FS, CHI11-05-02-310: FS, CHI11-05-02-215: FS, CHI11-05-02-260: FS | CHI11-05-02-295, CHI11-05-02-305, CHI11-05-02-310, CHI11-05-02-215, CHI11-05-02-260
COLO 5 - CELL 3 |  | 89 | 89 | 2025-05-01 | 2025-08-21 | 5
COLO 5 - CELL 3 Data Hall |  | 79 | 79 | 2025-05-01 | 2025-08-08 | 5
CHI11-05-03-10 | C05/03-DH- Layout Framing | 1 | 1 | 2025-05-01 | 2025-05-01 | 26 | CHI11-05-04-40: FS | CHI11-05-04-40
CHI11-05-03-15 | C05/03-DH- Install Framing | 3 | 3 | 2025-05-02 | 2025-05-06 | 26 | CHI11-05-03-10: FS | CHI11-05-03-10
CHI11-05-03-20 | C05/03-DH- In-Wall R/I | 3 | 3 | 2025-05-07 | 2025-05-09 | 26 | CHI11-05-03-15: FS | CHI11-05-03-15
CHI11-05-03-35 | C05/03-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-05-10 | 2025-05-13 | 26 | CHI11-05-03-20: FS | CHI11-05-03-20
CHI11-05-03-40 | C05/03-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-05-10 | 2025-05-13 | 26 | CHI11-05-03-20: FS | CHI11-05-03-20
CHI11-05-03-55 | C05/03-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-05-14 | 2025-05-16 | 31 | CHI11-05-03-35: FS | CHI11-05-03-35
CHI11-05-03-60 | C05/03-DH- Overhead R/I - Electrical | 4 | 4 | 2025-05-14 | 2025-05-17 | 31 | CHI11-05-03-55: SS | CHI11-05-03-55
CHI11-05-03-65 | C05/03-DH- Finish Dry-Wall | 3 | 3 | 2025-05-14 | 2025-05-16 | 26 | CHI11-05-03-40: FS | CHI11-05-03-40
CHI11-05-03-85 | C05/03-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-05-16 | 2025-05-17 | 31 | CHI11-05-03-60: FF | CHI11-05-03-60
CHI11-05-03-90 | C05/03-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-05-16 | 2025-05-17 | 31 | CHI11-05-03-85: FF, CHI11-05-03-60: FF | CHI11-05-03-85, CHI11-05-03-60
CHI11-05-03-115 | C05/03-DH- Paint Dry-Wall | 3 | 3 | 2025-05-17 | 2025-05-20 | 26 | CHI11-05-03-65: FS | CHI11-05-03-65
CHI11-05-03-135 | C05/03-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-05-21 | 2025-05-23 | 26 | CHI11-05-03-115: FS | CHI11-05-03-115
CHI11-05-03-150 | C05/03-DH- Install Secondary Steel | 1 | 1 | 2025-05-27 | 2025-05-27 | 26 | CHI11-05-03-90: FS, CHI11-05-03-135: FS | CHI11-05-03-90, CHI11-05-03-135
CHI11-05-03-155 | C05/03-DH- Paint Secondary Steel | 2 | 2 | 2025-05-28 | 2025-05-29 | 26 | CHI11-05-03-150: FS | CHI11-05-03-150
CHI11-05-03-165 | C05/03-DH- General Cleaning | 1 | 1 | 2025-05-30 | 2025-05-30 | 29 | CHI11-05-03-155: FS | CHI11-05-03-155
CHI11-05-03-170 | C05/03-DH- Install Ceiling Grid | 4 | 4 | 2025-05-30 | 2025-06-03 | 26 | CHI11-05-03-85: FS, CHI11-05-03-90: FS, CHI11-05-03-155: FS | CHI11-05-03-85, CHI11-05-03-90, CHI11-05-03-155
CHI11-05-03-180 | C05/03-DH- Install Perimeter Cable Trays | 4 | 4 | 2025-06-04 | 2025-06-07 | 29 | CHI11-05-03-170: FS | CHI11-05-03-170
CHI11-05-03-185 | C05/03-DH- Assemble HACs [Qty - 5] | 5 | 5 | 2025-06-04 | 2025-06-09 | 26 | CHI11-05-03-170: FS, CHI11-05-03-165: FS | CHI11-05-03-170, CHI11-05-03-165
CHI11-05-03-205 | C05/03-DH- Install Busways on HAC Arms | 5 | 5 | 2025-06-06 | 2025-06-11 | 26 | CHI11-05-03-185: FF 2 | CHI11-05-03-185
CHI11-05-03-215 | C05/03-DH- Install Device Tiles | 2 | 2 | 2025-06-09 | 2025-06-10 | 29 | CHI11-05-03-180: FS | CHI11-05-03-180
CHI11-05-03-220 | C05/03-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-06-09 | 2025-06-13 | 26 | CHI11-05-03-205: FF 2 | CHI11-05-03-205
CHI11-05-03-225 | C05/03-DH- Set PDUs | 4 | 4 | 2025-06-09 | 2025-06-12 | 34 | CHI11-05-03-180: FS | CHI11-05-03-180
CHI11-05-03-250 | C05/03-DH- Raise HACs | 4 | 4 | 2025-06-16 | 2025-06-19 | 26 | CHI11-05-03-215: FS, CHI11-05-03-220: FS | CHI11-05-03-215, CHI11-05-03-220
CHI11-05-03-260 | C05/03-DH- Detail HACs | 4 | 4 | 2025-06-20 | 2025-06-24 | 41 | CHI11-05-03-250: FS | CHI11-05-03-250
CHI11-05-03-265 | C05/03-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-06-20 | 2025-06-23 | 26 | CHI11-05-03-250: FS | CHI11-05-03-250
CHI11-05-03-275 | C05/03-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-06-24 | 2025-06-26 | 26 | CHI11-05-03-225: FS, CHI11-05-03-265: FS | CHI11-05-03-225, CHI11-05-03-265
CHI11-05-03-285 | C05/03-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-06-27 | 2025-07-02 | 26 | CHI11-05-03-275: FS | CHI11-05-03-275
CHI11-05-03-310 | C05/03-DH- Terminate PDUs | 3 | 3 | 2025-08-06 | 2025-08-08 | 0 | CHI11-05-03-285: FS, CHI11-05-03-305: FS | CHI11-05-03-285, CHI11-05-03-305
COLO 5 - CELL 3 Electrical Room |  | 72 | 72 | 2025-05-07 | 2025-08-05 | 0
CHI11-05-03-25 | C05/03-Elec Rm- Install Framing | 2 | 2 | 2025-05-07 | 2025-05-08 | 26 | CHI11-05-03-15: FS | CHI11-05-03-15
CHI11-05-03-30 | C05/03-Elec Rm- In-Wall R/I | 2 | 2 | 2025-05-09 | 2025-05-10 | 26 | CHI11-05-03-25: FS | CHI11-05-03-25
CHI11-05-03-45 | C05/03-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-05-12 | 2025-05-13 | 26 | CHI11-05-03-30: FS | CHI11-05-03-30
CHI11-05-03-50 | C05/03-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-05-12 | 2025-05-15 | 35 | CHI11-05-03-30: FS | CHI11-05-03-30
CHI11-05-03-70 | C05/03-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-05-14 | 2025-05-15 | 37 | CHI11-05-03-45: FS | CHI11-05-03-45
CHI11-05-03-75 | C05/03-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-05-14 | 2025-05-16 | 37 | CHI11-05-03-70: SS | CHI11-05-03-70
CHI11-05-03-95 | C05/03-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-05-16 | 2025-05-17 | 35 | CHI11-05-03-50: FS | CHI11-05-03-50
CHI11-05-03-100 | C05/03-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-05-16 | 2025-05-16 | 37 | CHI11-05-03-75: FF | CHI11-05-03-75
CHI11-05-03-120 | C05/03-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-05-17 | 2025-05-19 | 37 | CHI11-05-03-100: FS | CHI11-05-03-100
CHI11-05-03-125 | C05/03-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-05-19 | 2025-05-20 | 35 | CHI11-05-03-95: FS | CHI11-05-03-95
CHI11-05-03-140 | C05/03-Elec Rm- General Cleaning | 1 | 1 | 2025-05-21 | 2025-05-21 | 35 | CHI11-05-03-125: FS | CHI11-05-03-125
CHI11-05-03-145 | C05/03-Elec Rm- Set Electrical Equipments | 3 | 3 | 2025-05-22 | 2025-05-27 | 35 | CHI11-05-03-140: FS, CHI11-05-03-120: FS | CHI11-05-03-140, CHI11-05-03-120
CHI11-05-03-295 | C05/03-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | 11 | 11 | 2025-07-11 | 2025-07-23 | 0 | CHI11-05-04-305: FS, CHI11-05-03-145: FS | CHI11-05-04-305, CHI11-05-03-145
CHI11-05-03-300 | C05/03-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-07-24 | 2025-07-29 | 0 | CHI11-05-03-295: FS | CHI11-05-03-295
CHI11-05-03-305 | C05/03-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | 10 | 10 | 2025-07-24 | 2025-08-05 | 0 | CHI11-05-03-295: FS, CHI11-05-03-300: SS | CHI11-05-03-295, CHI11-05-03-300
COLO 5 - CELL 3 Mechanical Gallery |  | 43 | 43 | 2025-05-14 | 2025-07-08 | 26
CHI11-05-03-80 | C05/03-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-05-14 | 2025-05-15 | 26 | CHI11-05-03-45: FS, CHI11-05-03-35: FS | CHI11-05-03-45, CHI11-05-03-35
CHI11-05-03-105 | C05/03-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-05-16 | 2025-05-17 | 26 | CHI11-05-03-80: FS | CHI11-05-03-80
CHI11-05-03-110 | C05/03-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-05-16 | 2025-05-19 | 26 | CHI11-05-03-105: SS | CHI11-05-03-105
CHI11-05-03-130 | C05/03-Mech Gallery- Overhead R/I - Mechanical | 5 | 5 | 2025-05-20 | 2025-05-27 | 26 | CHI11-05-03-110: FS | CHI11-05-03-110
CHI11-05-03-160 | C05/03-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-05-28 | 2025-06-03 | 26 | CHI11-05-03-130: FS | CHI11-05-03-130
CHI11-05-03-175 | C05/03-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-06-02 | 2025-06-03 | 26 | CHI11-05-03-160: FF, CHI11-05-03-20: FS | CHI11-05-03-160, CHI11-05-03-20
CHI11-05-03-190 | C05/03-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-06-04 | 2025-06-05 | 26 | CHI11-05-03-175: FS | CHI11-05-03-175
CHI11-05-03-195 | C05/03-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-06-04 | 2025-06-04 | 26 | CHI11-05-03-160: FS, CHI11-05-03-110: FF | CHI11-05-03-160, CHI11-05-03-110
CHI11-05-03-200 | C05/03-Mech Gallery- Install Ceiling Grid + Device Tiles | 4 | 4 | 2025-06-05 | 2025-06-09 | 26 | CHI11-05-03-195: FS | CHI11-05-03-195
CHI11-05-03-210 | C05/03-Mech Gallery- Paint Dry-Wall | 2 | 2 | 2025-06-06 | 2025-06-07 | 26 | CHI11-05-03-190: FS | CHI11-05-03-190
CHI11-05-03-230 | C05/03-Mech Gallery- General Cleaning | 3 | 3 | 2025-06-09 | 2025-06-11 | 26 | CHI11-05-03-210: FS | CHI11-05-03-210
CHI11-05-03-235 | C05/03-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-06-10 | 2025-06-11 | 26 | CHI11-05-03-200: FS, CHI11-05-03-195: FS | CHI11-05-03-200, CHI11-05-03-195
CHI11-05-03-240 | C05/03-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-06-10 | 2025-06-21 | 30 | CHI11-05-03-200: FS | CHI11-05-03-200
CHI11-05-03-245 | C05/03-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-06-12 | 2025-06-17 | 26 | CHI11-05-03-230: FS, CHI11-05-03-235: FS | CHI11-05-03-230, CHI11-05-03-235
CHI11-05-03-255 | C05/03-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-06-18 | 2025-07-01 | 26 | CHI11-05-03-245: FS | CHI11-05-03-245
CHI11-05-03-270 | C05/03-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-06-23 | 2025-07-01 | 30 | CHI11-05-03-240: FS | CHI11-05-03-240
CHI11-05-03-290 | C05/03-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-07-02 | 2025-07-08 | 26 | CHI11-05-03-255: FS | CHI11-05-03-255
COLO 5 - CELL 3 Punchlist |  | 10 | 10 | 2025-08-09 | 2025-08-21 | 5
CHI11-05-03-280 | C05/03- Punchlist | 10 | 10 | 2025-08-09 | 2025-08-21 | 5 | CHI11-05-03-290: FS, CHI11-05-03-305: FS, CHI11-05-03-310: FS, CHI11-05-03-215: FS, CHI11-05-03-260: FS | CHI11-05-03-290, CHI11-05-03-305, CHI11-05-03-310, CHI11-05-03-215, CHI11-05-03-260
COLO 5 - CELL 4 |  | 78 | 78 | 2025-04-19 | 2025-07-25 | 18
COLO 5 - CELL 4 Data Hall Fitout Activities |  | 68 | 68 | 2025-04-19 | 2025-07-14 | 18
CHI11-05-04-10 | C05/04-DH- Layout Framing | 1 | 1 | 2025-04-19 | 2025-04-19 | 22 | CHI11-05-02-40: SS 2 | CHI11-05-02-40
CHI11-05-04-15 | C05/04-DH- Install Framing | 3 | 3 | 2025-04-21 | 2025-04-23 | 22 | CHI11-05-04-10: FS | CHI11-05-04-10
CHI11-05-04-20 | C05/04-DH- In-Wall R/I | 3 | 3 | 2025-04-24 | 2025-04-26 | 26 | CHI11-05-04-15: FS | CHI11-05-04-15
CHI11-05-04-35 | C05/04-DH- Overhead R/I - Fire Protection | 3 | 3 | 2025-04-28 | 2025-04-30 | 28 | CHI11-05-04-20: FS | CHI11-05-04-20
CHI11-05-04-40 | C05/04-DH- Install Drywall (One Side - Facing DH) | 3 | 3 | 2025-04-28 | 2025-04-30 | 26 | CHI11-05-04-20: FS | CHI11-05-04-20
CHI11-05-04-55 | C05/04-DH- Overhead R/I - Fire Alarm | 3 | 3 | 2025-05-01 | 2025-05-05 | 33 | CHI11-05-04-35: FS | CHI11-05-04-35
CHI11-05-04-60 | C05/04-DH- Overhead R/I - Electrical | 4 | 4 | 2025-05-01 | 2025-05-06 | 33 | CHI11-05-04-55: SS | CHI11-05-04-55
CHI11-05-04-65 | C05/04-DH- Finish Dry-Wall | 3 | 3 | 2025-05-01 | 2025-05-05 | 28 | CHI11-05-04-40: FS | CHI11-05-04-40
CHI11-05-04-85 | C05/04-DH- Overhead R/I - Mechanical | 2 | 2 | 2025-05-05 | 2025-05-06 | 33 | CHI11-05-04-60: FF | CHI11-05-04-60
CHI11-05-04-90 | C05/04-DH- Drop Cable Tray [Hanging Rods] | 2 | 2 | 2025-05-05 | 2025-05-06 | 33 | CHI11-05-04-85: FF, CHI11-05-04-60: FF | CHI11-05-04-85, CHI11-05-04-60
CHI11-05-04-115 | C05/04-DH- Paint Dry-Wall | 3 | 3 | 2025-05-06 | 2025-05-08 | 28 | CHI11-05-04-65: FS | CHI11-05-04-65
CHI11-05-04-135 | C05/04-DH- Install Screen Mesh + Caulking | 3 | 3 | 2025-05-09 | 2025-05-12 | 28 | CHI11-05-04-115: FS | CHI11-05-04-115
CHI11-05-04-150 | C05/04-DH- Install Secondary Steel | 2 | 2 | 2025-05-13 | 2025-05-14 | 28 | CHI11-05-04-90: FS, CHI11-05-04-135: FS | CHI11-05-04-90, CHI11-05-04-135
CHI11-05-04-155 | C05/04-DH- Paint Secondary Steel | 2 | 2 | 2025-05-15 | 2025-05-16 | 28 | CHI11-05-04-150: FS | CHI11-05-04-150
CHI11-05-04-165 | C05/04-DH- General Cleaning | 1 | 1 | 2025-05-17 | 2025-05-17 | 31 | CHI11-05-04-155: FS | CHI11-05-04-155
CHI11-05-04-170 | C05/04-DH- Install Ceiling Grid | 4 | 4 | 2025-05-17 | 2025-05-21 | 28 | CHI11-05-04-85: FS, CHI11-05-04-90: FS, CHI11-05-04-155: FS | CHI11-05-04-85, CHI11-05-04-90, CHI11-05-04-155
CHI11-05-04-180 | C05/04-DH- Install Perimeter Cable Trays | 3 | 3 | 2025-05-22 | 2025-05-27 | 31 | CHI11-05-04-170: FS | CHI11-05-04-170
CHI11-05-04-185 | C05/04-DH- Assemble HACs [Qty - 5] | 4 | 4 | 2025-05-22 | 2025-05-28 | 28 | CHI11-05-04-170: FS, CHI11-05-04-165: FS | CHI11-05-04-170, CHI11-05-04-165
CHI11-05-04-205 | C05/04-DH- Install Busways on HAC Arms | 4 | 4 | 2025-05-27 | 2025-05-30 | 28 | CHI11-05-04-185: FF 2 | CHI11-05-04-185
CHI11-05-04-215 | C05/04-DH- Install Device Tiles | 2 | 2 | 2025-05-28 | 2025-05-29 | 31 | CHI11-05-04-180: FS | CHI11-05-04-180
CHI11-05-04-220 | C05/04-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | 5 | 5 | 2025-05-28 | 2025-06-02 | 28 | CHI11-05-04-205: FF 2 | CHI11-05-04-205
CHI11-05-04-225 | C05/04-DH- Set PDUs | 4 | 4 | 2025-05-28 | 2025-05-31 | 36 | CHI11-05-04-180: FS | CHI11-05-04-180
CHI11-05-04-250 | C05/04-DH- Raise HACs | 4 | 4 | 2025-06-03 | 2025-06-06 | 28 | CHI11-05-04-215: FS, CHI11-05-04-220: FS | CHI11-05-04-215, CHI11-05-04-220
CHI11-05-04-260 | C05/04-DH- Detail HACs | 4 | 4 | 2025-06-07 | 2025-06-11 | 43 | CHI11-05-04-250: FS | CHI11-05-04-250
CHI11-05-04-265 | C05/04-DH- Connect Perimeter Cable Trays to HAC Cable Trays | 3 | 3 | 2025-06-07 | 2025-06-10 | 28 | CHI11-05-04-250: FS | CHI11-05-04-250
CHI11-05-04-275 | C05/04-DH- Install Conduits PDU to Cable Trays | 3 | 3 | 2025-06-11 | 2025-06-13 | 28 | CHI11-05-04-225: FS, CHI11-05-04-265: FS | CHI11-05-04-225, CHI11-05-04-265
CHI11-05-04-290 | C05/04-DH- Pull Feeders from PDUs to Busways | 5 | 5 | 2025-06-16 | 2025-06-20 | 28 | CHI11-05-04-275: FS | CHI11-05-04-275
CHI11-05-04-310 | C05/04-DH- Terminate PDUs | 3 | 3 | 2025-07-11 | 2025-07-14 | 13 | CHI11-05-04-290: FS, CHI11-05-04-305: FS | CHI11-05-04-290, CHI11-05-04-305
COLO 5 - CELL 4 Electrical Room |  | 61 | 61 | 2025-04-24 | 2025-07-10 | 0
CHI11-05-04-25 | C05/04-Elec Rm- Install Framing | 2 | 2 | 2025-04-24 | 2025-04-25 | 22 | CHI11-05-04-15: FS | CHI11-05-04-15
CHI11-05-04-30 | C05/04-Elec Rm- In-Wall R/I | 2 | 2 | 2025-04-26 | 2025-04-28 | 22 | CHI11-05-04-25: FS | CHI11-05-04-25
CHI11-05-04-45 | C05/04-Elec Rm- Overhead R/I - Fire Protection | 2 | 2 | 2025-04-29 | 2025-04-30 | 24 | CHI11-05-04-30: FS | CHI11-05-04-30
CHI11-05-04-50 | C05/04-Elec Rm- Install Drywall [Elec + Battery Rooms] | 4 | 4 | 2025-04-29 | 2025-05-02 | 22 | CHI11-05-04-30: FS | CHI11-05-04-30
CHI11-05-04-70 | C05/04-Elec Rm- Overhead R/I - Fire Alarm | 2 | 2 | 2025-05-01 | 2025-05-02 | 24 | CHI11-05-04-45: FS | CHI11-05-04-45
CHI11-05-04-75 | C05/04-Elec Rm- Overhead R/I - Electrical | 3 | 3 | 2025-05-01 | 2025-05-05 | 24 | CHI11-05-04-70: SS | CHI11-05-04-70
CHI11-05-04-95 | C05/04-Elec Rm- Finish Dry-Wall | 2 | 2 | 2025-05-05 | 2025-05-06 | 22 | CHI11-05-04-50: FS | CHI11-05-04-50
CHI11-05-04-100 | C05/04-Elec Rm- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-05-05 | 2025-05-05 | 24 | CHI11-05-04-75: FF | CHI11-05-04-75
CHI11-05-04-120 | C05/04-Elec Rm- Install Cable Trays / Pathways | 2 | 2 | 2025-05-06 | 2025-05-07 | 24 | CHI11-05-04-100: FS | CHI11-05-04-100
CHI11-05-04-125 | C05/04-Elec Rm- Paint Dry-Wall | 2 | 2 | 2025-05-07 | 2025-05-08 | 22 | CHI11-05-04-95: FS | CHI11-05-04-95
CHI11-05-04-140 | C05/04-Elec Rm- General Cleaning | 1 | 1 | 2025-05-09 | 2025-05-09 | 22 | CHI11-05-04-125: FS | CHI11-05-04-125
CHI11-05-04-145 | C05/04-Elec Rm- Set Electrical Equipments | 4 | 4 | 2025-05-10 | 2025-05-14 | 22 | CHI11-05-04-140: FS, CHI11-05-04-120: FS | CHI11-05-04-140, CHI11-05-04-120
CHI11-05-04-280 | C05/04-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | 11 | 11 | 2025-06-12 | 2025-06-25 | 0 | CHI11-05-02-305: SS, CHI11-05-04-145: FS | CHI11-05-02-305, CHI11-05-04-145
CHI11-05-04-300 | C05/04-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | 4 | 4 | 2025-06-26 | 2025-06-30 | 0 | CHI11-05-04-280: FS | CHI11-05-04-280
CHI11-05-04-305 | C05/04-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | 11 | 11 | 2025-06-26 | 2025-07-10 | 0 | CHI11-05-04-280: FS, CHI11-05-04-300: SS | CHI11-05-04-280, CHI11-05-04-300
COLO 5 - CELL 4 Mechanical Gallery |  | 43 | 43 | 2025-05-01 | 2025-06-24 | 28
CHI11-05-04-80 | C05/04-Mech Gallery- Overhead R/I - Fire Protection | 2 | 2 | 2025-05-01 | 2025-05-02 | 28 | CHI11-05-04-45: FS, CHI11-05-04-35: FS | CHI11-05-04-45, CHI11-05-04-35
CHI11-05-04-105 | C05/04-Mech Gallery- Overhead R/I - Fire Alarm | 2 | 2 | 2025-05-05 | 2025-05-06 | 28 | CHI11-05-04-80: FS | CHI11-05-04-80
CHI11-05-04-110 | C05/04-Mech Gallery- Overhead R/I - Electrical | 3 | 3 | 2025-05-05 | 2025-05-07 | 28 | CHI11-05-04-105: SS | CHI11-05-04-105
CHI11-05-04-130 | C05/04-Mech Gallery- Overhead R/I - Mechanical | 6 | 6 | 2025-05-08 | 2025-05-14 | 28 | CHI11-05-04-110: FS | CHI11-05-04-110
CHI11-05-04-160 | C05/04-Mech Gallery- Overhead R/I - Plumbing | 6 | 6 | 2025-05-15 | 2025-05-21 | 28 | CHI11-05-04-130: FS | CHI11-05-04-130
CHI11-05-04-175 | C05/04-Mech Gallery- Install Drywall [Mech Gallery] | 2 | 2 | 2025-05-20 | 2025-05-21 | 28 | CHI11-05-04-160: FF, CHI11-05-04-20: FS | CHI11-05-04-160, CHI11-05-04-20
CHI11-05-04-190 | C05/04-Mech Gallery- Finish Dry-Wall | 2 | 2 | 2025-05-22 | 2025-05-23 | 28 | CHI11-05-04-175: FS | CHI11-05-04-175
CHI11-05-04-195 | C05/04-Mech Gallery- Drop Cable Tray [Hanging Rods] | 1 | 1 | 2025-05-22 | 2025-05-22 | 28 | CHI11-05-04-160: FS, CHI11-05-04-110: FF | CHI11-05-04-160, CHI11-05-04-110
CHI11-05-04-200 | C05/04-Mech Gallery- Install Ceiling Grid + Device Tiles | 3 | 3 | 2025-05-23 | 2025-05-28 | 28 | CHI11-05-04-195: FS | CHI11-05-04-195
CHI11-05-04-210 | C05/04-Mech Gallery- Paint Dry-Wall | 1 | 1 | 2025-05-27 | 2025-05-27 | 28 | CHI11-05-04-190: FS | CHI11-05-04-190
CHI11-05-04-230 | C05/04-Mech Gallery- General Cleaning | 3 | 3 | 2025-05-28 | 2025-05-30 | 28 | CHI11-05-04-210: FS | CHI11-05-04-210
CHI11-05-04-235 | C05/04-Mech Gallery- Install Cable Trays / Pathways | 2 | 2 | 2025-05-29 | 2025-05-30 | 28 | CHI11-05-04-200: FS, CHI11-05-04-195: FS | CHI11-05-04-200, CHI11-05-04-195
CHI11-05-04-240 | C05/04-Mech Gallery- Install BAS Equipments | 10 | 10 | 2025-05-29 | 2025-06-09 | 32 | CHI-11-05-ROJ-F: FS, CHI11-05-04-200: FS | CHI-11-05-ROJ-F, CHI11-05-04-200
CHI11-05-04-245 | C05/04-Mech Gallery- Set Mechanical Equipments | 4 | 4 | 2025-05-31 | 2025-06-04 | 28 | CHI11-05-04-230: FS, CHI11-05-04-235: FS | CHI11-05-04-230, CHI11-05-04-235
CHI11-05-04-255 | C05/04-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | 12 | 12 | 2025-06-05 | 2025-06-19 | 28 | CHI11-05-04-245: FS | CHI11-05-04-245
CHI11-05-04-270 | C05/04-Mech Gallery- Pull & Terminate BAS Equipments | 8 | 8 | 2025-06-10 | 2025-06-19 | 32 | CHI11-05-04-240: FS | CHI11-05-04-240
CHI11-05-04-295 | C05/04-Mech Gallery- Terminate Mechanical Equipments | 4 | 4 | 2025-06-20 | 2025-06-24 | 28 | CHI11-05-04-255: FS | CHI11-05-04-255
COLO 5 - CELL 4 Punchlist |  | 10 | 10 | 2025-07-15 | 2025-07-25 | 18
CHI11-05-04-285 | C05/04- Punchlist | 10 | 10 | 2025-07-15 | 2025-07-25 | 18 | CHI11-05-04-295: FS, CHI11-05-04-305: FS, CHI11-05-04-310: FS, CHI11-05-04-215: FS, CHI11-05-04-260: FS | CHI11-05-04-295, CHI11-05-04-305, CHI11-05-04-310, CHI11-05-04-215, CHI11-05-04-260
Commissioning (L2- L5) |  | 159 | 159 | 2025-05-05 | 2025-11-19 | 0
COLO 3 |  | 109 | 109 | 2025-05-05 | 2025-09-18 | 0
Yellow Tags (Level 2) |  | 48 | 48 | 2025-05-05 | 2025-07-02 | 0
CHI11-03-01-315 | C03/01-L2Cx- Yellow Tags | 19 | 19 | 2025-05-05 | 2025-05-28 | 13 | CHI11-ADMIN-490: FS, CHI11-03-01-285: FS, CHI11-03-01-310: FS, CHI11-03-01-300: FS, CHI11-03-01-290: FS, CHI11-03-YARD-50: SS 7, CHI11-03-01-305: FS, CHI11-ADMIN-455: FS | CHI11-ADMIN-490, CHI11-03-01-285, CHI11-03-01-310, CHI11-03-01-300, CHI11-03-01-290, CHI11-03-YARD-50, CHI11-03-01-305, CHI11-ADMIN-455
CHI11-03-02-315 | C03/02-L2Cx- Yellow Tags | 19 | 19 | 2025-05-15 | 2025-06-07 | 9 | CHI-11-03-L2CX-S: SS, CHI11-03-02-270: FS, CHI11-03-02-280: SS, CHI11-03-02-310: FS, CHI11-03-02-290: FS, CHI11-03-YARD-55: FS, CHI11-03-01-315: SS 5 | CHI-11-03-L2CX-S, CHI11-03-02-270, CHI11-03-02-280, CHI11-03-02-310, CHI11-03-02-290, CHI11-03-YARD-55, CHI11-03-01-315
CHI11-03-04-315 | C03/04-L2Cx- Yellow Tags | 19 | 19 | 2025-05-27 | 2025-06-18 | 6 | CHI11-03-04-290: FS, CHI11-03-04-310: FS, CHI11-03-04-240: FS, CHI11-03-04-280: FS, CHI11-03-04-300: FS, CHI11-03-YARD-60: FS, CHI11-03-02-315: SS 5 | CHI11-03-04-290, CHI11-03-04-310, CHI11-03-04-240, CHI11-03-04-280, CHI11-03-04-300, CHI11-03-YARD-60, CHI11-03-02-315
CHI11-03-03-315 | C03/03-L2Cx- Yellow Tags | 20 | 20 | 2025-06-09 | 2025-07-02 | 0 | CHI11-03-01-300: FS, CHI11-03-02-290: FS, CHI11-03-04-300: FS, CHI11-03-03-305: FS, CHI-11-03-ROJ-F: FS, CHI11-ADMIN-485: FF, CHI11-03-03-280: SS, CHI11-03-03-310: FS, CHI11-03-03-300: FS, CHI11-03-03-270: FS, CHI11-03-03-290: FS, CHI11-03-YARD-65: FS, CHI11-03-04-315: SS 5 | CHI11-03-01-300, CHI11-03-02-290, CHI11-03-04-300, CHI11-03-03-305, CHI-11-03-ROJ-F, CHI11-ADMIN-485, CHI11-03-03-280, CHI11-03-03-310, CHI11-03-03-300, CHI11-03-03-270, CHI11-03-03-290, CHI11-03-YARD-65, CHI11-03-04-315
Energizations & Startups (Level 3) |  | 58 | 58 | 2025-06-04 | 2025-08-14 | 0
CHI11-03-L3-10 | C03-L3Cx- Install Metering Cabinet [Prior to Energization] | 5 | 5 | 2025-06-19 | 2025-06-24 | 8 | CHI-11-CFCI-10: FS | CHI-11-CFCI-10
COLO 3 - CELL 1 |  | 37 | 37 | 2025-06-04 | 2025-07-19 | 8
CHI11-03-01-320 | C03/01-L3Cx- Control Power Checks | 8 | 8 | 2025-06-04 | 2025-06-12 | 9 | CHI-11-03-POW-F: FS, CHI11-SU-50: SS, CHI11-03-02-315: SS 15, CHI11-03-01-315: FS, CHI-11-MS-06: FS | CHI-11-03-POW-F, CHI11-SU-50, CHI11-03-02-315, CHI11-03-01-315, CHI-11-MS-06
CHI11-03-01-325 | C03/01-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-06-13 | 2025-06-23 | 9 | CHI11-03-01-320: FS | CHI11-03-01-320
CHI11-03-01-330 | C03/01-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-06-25 | 2025-06-28 | 8 | CHI11-03-01-325: FS, CHI11-03-L3-10: FS | CHI11-03-01-325, CHI11-03-L3-10
CHI11-03-01-335 | C03/01-L3Cx- Startups | 12 | 12 | 2025-06-30 | 2025-07-15 | 8 | CHI11-03-01-330: FS | CHI11-03-01-330
CHI11-03-01-340 | C03/01-L3Cx- Loadbanking | 4 | 4 | 2025-07-16 | 2025-07-19 | 8 | CHI11-03-01-335: FS | CHI11-03-01-335
COLO 3 - CELL 2 |  | 37 | 37 | 2025-06-09 | 2025-07-24 | 8
CHI11-03-02-320 | C03/02-L3Cx- Control Power Checks | 8 | 8 | 2025-06-09 | 2025-06-18 | 9 | CHI-11-03-L3CX-S: SS, CHI11-03-02-315: FS | CHI-11-03-L3CX-S, CHI11-03-02-315
CHI11-03-02-325 | C03/02-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-06-19 | 2025-06-27 | 9 | CHI11-03-02-320: FS | CHI11-03-02-320
CHI11-03-02-330 | C03/02-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-06-28 | 2025-07-02 | 9 | CHI11-03-02-325: FS | CHI11-03-02-325
CHI11-03-02-335 | C03/02-L3Cx- Startups | 12 | 12 | 2025-07-03 | 2025-07-18 | 9 | CHI11-03-02-330: FS | CHI11-03-02-330
CHI11-03-02-340 | C03/02-L3Cx- Loadbanking | 4 | 4 | 2025-07-21 | 2025-07-24 | 8 | CHI11-03-01-340: FS, CHI11-03-02-335: FS | CHI11-03-01-340, CHI11-03-02-335
COLO 3 - CELL 4 |  | 37 | 37 | 2025-06-13 | 2025-07-30 | 8
CHI11-03-04-320 | C03/04-L3Cx- Control Power Checks | 8 | 8 | 2025-06-13 | 2025-06-23 | 9 | CHI11-03-04-315: SS 15 | CHI11-03-04-315
CHI11-03-04-325 | C03/04-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-06-24 | 2025-07-02 | 9 | CHI11-03-04-320: FS | CHI11-03-04-320
CHI11-03-04-330 | C03/04-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-07-03 | 2025-07-09 | 9 | CHI11-03-04-325: FS | CHI11-03-04-325
CHI11-03-04-335 | C03/04-L3Cx- Startups | 12 | 12 | 2025-07-10 | 2025-07-23 | 9 | CHI11-03-04-330: FS | CHI11-03-04-330
CHI11-03-04-340 | C03/04-L3Cx- Loadbanking | 4 | 4 | 2025-07-25 | 2025-07-30 | 8 | CHI11-03-02-340: FS, CHI11-03-04-335: FS | CHI11-03-02-340, CHI11-03-04-335
COLO 3 - CELL 3 |  | 42 | 42 | 2025-06-24 | 2025-08-14 | 0
CHI11-03-03-320 | C03/03-L3Cx- Control Power Checks | 10 | 10 | 2025-06-24 | 2025-07-07 | 0 | CHI11-03-03-315: SS 12 | CHI11-03-03-315
CHI11-03-03-325 | C03/03-L3Cx- EPMS Point to Point Checks | 10 | 10 | 2025-07-08 | 2025-07-18 | 0 | CHI11-03-03-320: FS | CHI11-03-03-320
CHI11-03-03-330 | C03/03-L3Cx- FTE Energizations [480v] | 5 | 5 | 2025-07-19 | 2025-07-24 | 0 | CHI11-03-03-325: FS | CHI11-03-03-325
CHI11-03-03-335 | C03/03-L3Cx- Startups | 12 | 12 | 2025-07-25 | 2025-08-08 | 0 | CHI11-03-03-330: FS | CHI11-03-03-330
CHI11-03-03-340 | C03/03-L3Cx- Loadbanking | 5 | 5 | 2025-08-09 | 2025-08-14 | 0 | CHI11-03-04-340: FS, CHI11-03-03-335: FS | CHI11-03-04-340, CHI11-03-03-335
Functional Testing (Level 4 & 5) |  | 27 | 27 | 2025-08-15 | 2025-09-18 | 0
CHI11-03-L4-10 | C03-L4Cx- Testing <MSFT Duration> | 24 | 24 | 2025-08-15 | 2025-09-15 | 0 | CHI11-03-04-340: FS, CHI11-03-02-340: FS, CHI11-03-01-340: FS, CHI11-03-03-340: FS | CHI11-03-04-340, CHI11-03-02-340, CHI11-03-01-340, CHI11-03-03-340
CHI11-03-L5-10 | C03-L5Cx- Testing <MSFT Duration> | 3 | 3 | 2025-09-16 | 2025-09-18 | 0 | CHI11-03-L4-10: FS | CHI11-03-L4-10
COLO 4 |  | 133 | 133 | 2025-05-06 | 2025-10-20 | 0
Yellow Tags (Level 2) |  | 81 | 81 | 2025-05-06 | 2025-08-14 | 0
CHI11-04-01-315 | C04/01-L2Cx- Yellow Tags | 19 | 19 | 2025-05-06 | 2025-05-29 | 26 | CHI11-04-01-275: FS, CHI11-04-01-295: FF 5, CHI11-04-01-305: FS, CHI11-04-01-285: FS, CHI11-04-YARD-50: FS, CHI11-04-01-310: FS | CHI11-04-01-275, CHI11-04-01-295, CHI11-04-01-305, CHI11-04-01-285, CHI11-04-YARD-50, CHI11-04-01-310
CHI11-04-02-315 | C04/02-L2Cx- Yellow Tags | 20 | 20 | 2025-05-31 | 2025-06-24 | 25 | CHI-11-04-L2CX-S: SS, CHI11-04-02-270: FS, CHI11-04-02-280: FF 5, CHI11-04-02-310: FS, CHI11-04-02-295: FS, CHI11-04-YARD-55: FS, CHI11-04-01-315: FS | CHI-11-04-L2CX-S, CHI11-04-02-270, CHI11-04-02-280, CHI11-04-02-310, CHI11-04-02-295, CHI11-04-YARD-55, CHI11-04-01-315
CHI11-04-04-315 | C04/04-L2Cx- Yellow Tags | 20 | 20 | 2025-06-27 | 2025-07-22 | 11 | CHI11-04-04-280: FF 5, CHI11-04-04-310: FS, CHI11-04-04-300: FS, CHI11-04-04-270: FS, CHI11-04-04-290: FS, CHI11-04-YARD-60: FS, CHI11-04-02-315: SS 8 | CHI11-04-04-280, CHI11-04-04-310, CHI11-04-04-300, CHI11-04-04-270, CHI11-04-04-290, CHI11-04-YARD-60, CHI11-04-02-315
CHI11-04-03-315 | C04/03-L2Cx- Yellow Tags | 20 | 20 | 2025-07-22 | 2025-08-14 | 0 | CHI11-04-03-280: FF 5, CHI11-04-03-310: FS, CHI11-04-03-300: FS, CHI11-04-03-270: FS, CHI11-04-03-290: FS, CHI11-04-YARD-65: FS, CHI11-04-04-315: SS 8 | CHI11-04-03-280, CHI11-04-03-310, CHI11-04-03-300, CHI11-04-03-270, CHI11-04-03-290, CHI11-04-YARD-65, CHI11-04-04-315
Energizations & Startups (Level 3) |  | 73 | 73 | 2025-06-20 | 2025-09-19 | 0
COLO 4 - CELL 1 |  | 36 | 36 | 2025-06-20 | 2025-08-04 | 25
CHI11-04-01-320 | C04/01-L3Cx- Control Power Checks | 8 | 8 | 2025-06-20 | 2025-06-28 | 25 | CHI11-04-02-315: SS 16, CHI11-04-01-315: FS | CHI11-04-02-315, CHI11-04-01-315
CHI11-04-01-325 | C04/01-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-06-30 | 2025-07-10 | 25 | CHI11-04-01-320: FS | CHI11-04-01-320
CHI11-04-01-330 | C04/01-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-07-11 | 2025-07-15 | 25 | CHI11-04-01-325: FS | CHI11-04-01-325
CHI11-04-01-335 | C04/01-L3Cx- Startups | 12 | 12 | 2025-07-16 | 2025-07-30 | 25 | CHI11-04-01-330: FS | CHI11-04-01-330
CHI11-04-01-340 | C04/01-L3Cx- Loadbanking | 4 | 4 | 2025-07-31 | 2025-08-04 | 25 | CHI11-04-01-335: FS | CHI11-04-01-335
COLO 4 - CELL 2 |  | 36 | 36 | 2025-06-25 | 2025-08-08 | 25
CHI11-04-02-320 | C04/02-L3Cx- Control Power Checks | 8 | 8 | 2025-06-25 | 2025-07-03 | 25 | CHI-11-04-L3CX-S: SS, CHI11-04-02-315: FS | CHI-11-04-L3CX-S, CHI11-04-02-315
CHI11-04-02-325 | C04/02-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-07-07 | 2025-07-15 | 25 | CHI11-04-02-320: FS | CHI11-04-02-320
CHI11-04-02-330 | C04/02-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-07-16 | 2025-07-19 | 25 | CHI11-04-02-325: FS | CHI11-04-02-325
CHI11-04-02-335 | C04/02-L3Cx- Startups | 12 | 12 | 2025-07-21 | 2025-08-04 | 25 | CHI11-04-02-330: FS | CHI11-04-02-330
CHI11-04-02-340 | C04/02-L3Cx- Loadbanking | 4 | 4 | 2025-08-05 | 2025-08-08 | 25 | CHI11-04-01-340: FS, CHI11-04-02-335: FS | CHI11-04-01-340, CHI11-04-02-335
COLO 4 - CELL 4 |  | 36 | 36 | 2025-07-18 | 2025-08-30 | 11
CHI11-04-04-320 | C04/04-L3Cx- Control Power Checks | 8 | 8 | 2025-07-18 | 2025-07-28 | 11 | CHI11-04-04-315: SS 16 | CHI11-04-04-315
CHI11-04-04-325 | C04/04-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-07-29 | 2025-08-06 | 11 | CHI11-04-04-320: FS | CHI11-04-04-320
CHI11-04-04-330 | C04/04-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-08-07 | 2025-08-11 | 11 | CHI11-04-04-325: FS | CHI11-04-04-325
CHI11-04-04-335 | C04/04-L3Cx- Startups | 12 | 12 | 2025-08-12 | 2025-08-26 | 11 | CHI11-04-04-330: FS | CHI11-04-04-330
CHI11-04-04-340 | C04/04-L3Cx- Loadbanking | 4 | 4 | 2025-08-27 | 2025-08-30 | 11 | CHI11-04-02-340: FS, CHI11-04-04-335: FS | CHI11-04-02-340, CHI11-04-04-335
COLO 4 - CELL 3 |  | 36 | 36 | 2025-08-06 | 2025-09-19 | 0
CHI11-04-03-320 | C04/03-L3Cx- Control Power Checks | 8 | 8 | 2025-08-06 | 2025-08-14 | 0 | CHI11-04-03-315: SS 12 | CHI11-04-03-315
CHI11-04-03-325 | C04/03-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-08-15 | 2025-08-25 | 0 | CHI11-04-03-320: FS | CHI11-04-03-320
CHI11-04-03-330 | C04/03-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-08-26 | 2025-08-29 | 0 | CHI11-04-03-325: FS | CHI11-04-03-325
CHI11-04-03-335 | C04/03-L3Cx- Startups | 12 | 12 | 2025-08-30 | 2025-09-15 | 0 | CHI11-04-03-330: FS | CHI11-04-03-330
CHI11-04-03-340 | C04/03-L3Cx- Loadbanking | 4 | 4 | 2025-09-16 | 2025-09-19 | 0 | CHI11-04-04-340: FS, CHI11-04-03-335: FS | CHI11-04-04-340, CHI11-04-03-335
Functional Testing (Level 4 & 5) |  | 24 | 24 | 2025-09-20 | 2025-10-20 | 0
CHI11-04-L4-10 | C04-L4Cx- Testing <MSFT Duration> | 22 | 22 | 2025-09-20 | 2025-10-16 | 0 | CHI11-03-L4-10: FS, CHI11-04-04-340: FS, CHI11-04-02-340: FS, CHI11-04-01-340: FS, CHI11-04-03-340: FS | CHI11-03-L4-10, CHI11-04-04-340, CHI11-04-02-340, CHI11-04-01-340, CHI11-04-03-340
CHI11-04-L5-10 | C04-L5Cx- Testing <MSFT Duration> | 2 | 2 | 2025-10-17 | 2025-10-20 | 0 | CHI11-04-L4-10: FS | CHI11-04-L4-10
COLO 5 |  | 134 | 134 | 2025-06-05 | 2025-11-19 | 0
Yellow Tags (Level 2) |  | 72 | 72 | 2025-06-05 | 2025-09-03 | 0
CHI11-05-01-315 | C05/01-L2Cx- Yellow Tags | 20 | 20 | 2025-06-05 | 2025-06-28 | 23 | CHI11-05-YARD-65: FF, CHI11-05-01-285: FS, CHI11-05-01-295: FF 5, CHI11-05-01-305: FS, CHI11-05-01-260: FS, CHI11-05-YARD-30: FS, CHI11-05-01-310: FS | CHI11-05-YARD-65, CHI11-05-01-285, CHI11-05-01-295, CHI11-05-01-305, CHI11-05-01-260, CHI11-05-YARD-30, CHI11-05-01-310
CHI11-05-02-315 | C05/02-L2Cx- Yellow Tags | 20 | 20 | 2025-06-28 | 2025-07-23 | 17 | CHI-11-05-L2CX-S: SS, CHI11-05-YARD-75: FF, CHI11-05-02-275: FS, CHI11-05-02-285: FF 5, CHI11-05-02-310: FS, CHI11-05-02-295: FS, CHI11-05-YARD-40: FS, CHI11-05-01-315: SS 13 | CHI-11-05-L2CX-S, CHI11-05-YARD-75, CHI11-05-02-275, CHI11-05-02-285, CHI11-05-02-310, CHI11-05-02-295, CHI11-05-YARD-40, CHI11-05-01-315
CHI11-05-04-315 | C05/04-L2Cx- Yellow Tags | 20 | 20 | 2025-07-15 | 2025-08-07 | 13 | CHI11-05-YARD-80: FF, CHI11-05-04-285: FF 5, CHI11-05-04-310: FS, CHI11-05-04-300: FS, CHI11-05-04-270: FS, CHI11-05-04-295: FS, CHI11-05-YARD-60: FS, CHI11-05-02-315: SS 8 | CHI11-05-YARD-80, CHI11-05-04-285, CHI11-05-04-310, CHI11-05-04-300, CHI11-05-04-270, CHI11-05-04-295, CHI11-05-YARD-60, CHI11-05-02-315
CHI11-05-03-315 | C05/03-L2Cx- Yellow Tags | 20 | 20 | 2025-08-09 | 2025-09-03 | 0 | CHI11-05-YARD-85: FF, CHI11-05-03-280: FF 5, CHI11-05-03-310: FS, CHI11-05-03-300: FS, CHI11-05-03-270: FS, CHI11-05-03-290: FS, CHI11-05-YARD-70: FS, CHI11-05-04-315: SS 8 | CHI11-05-YARD-85, CHI11-05-03-280, CHI11-05-03-310, CHI11-05-03-300, CHI11-05-03-270, CHI11-05-03-290, CHI11-05-YARD-70, CHI11-05-04-315
Energizations & Startups (Level 3) |  | 68 | 68 | 2025-07-19 | 2025-10-11 | 0
COLO 5 - CELL 1 |  | 36 | 36 | 2025-07-19 | 2025-09-02 | 18
CHI11-05-01-320 | C05/01-L3Cx- Control Power Checks | 8 | 8 | 2025-07-19 | 2025-07-29 | 18 | CHI11-05-02-315: SS 16, CHI11-05-01-315: FS | CHI11-05-02-315, CHI11-05-01-315
CHI11-05-01-325 | C05/01-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-07-30 | 2025-08-07 | 18 | CHI11-05-01-320: FS | CHI11-05-01-320
CHI11-05-01-330 | C05/01-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-08-08 | 2025-08-12 | 18 | CHI11-05-01-325: FS | CHI11-05-01-325
CHI11-05-01-335 | C05/01-L3Cx- Startups | 12 | 12 | 2025-08-13 | 2025-08-27 | 18 | CHI11-05-01-330: FS | CHI11-05-01-330
CHI11-05-01-340 | C05/01-L3Cx- Loadbanking | 4 | 4 | 2025-08-28 | 2025-09-02 | 18 | CHI11-05-01-335: FS | CHI11-05-01-335
COLO 5 - CELL 2 |  | 36 | 36 | 2025-07-24 | 2025-09-08 | 18
CHI11-05-02-320 | C05/02-L3Cx- Control Power Checks | 8 | 8 | 2025-07-24 | 2025-08-02 | 18 | CHI11-05-02-315: FS | CHI11-05-02-315
CHI11-05-02-325 | C05/02-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-08-04 | 2025-08-12 | 18 | CHI11-05-02-320: FS | CHI11-05-02-320
CHI11-05-02-330 | C05/02-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-08-13 | 2025-08-18 | 18 | CHI11-05-02-325: FS | CHI11-05-02-325
CHI11-05-02-335 | C05/02-L3Cx- Startups | 12 | 12 | 2025-08-19 | 2025-09-02 | 18 | CHI11-05-02-330: FS | CHI11-05-02-330
CHI11-05-02-340 | C05/02-L3Cx- Loadbanking | 4 | 4 | 2025-09-03 | 2025-09-08 | 18 | CHI11-05-01-340: FS, CHI11-05-02-335: FS | CHI11-05-01-340, CHI11-05-02-335
COLO 5 - CELL 4 |  | 36 | 36 | 2025-08-04 | 2025-09-17 | 14
CHI11-05-04-320 | C05/04-L3Cx- Control Power Checks | 8 | 8 | 2025-08-04 | 2025-08-12 | 14 | CHI11-05-04-315: SS 16 | CHI11-05-04-315
CHI11-05-04-325 | C05/04-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-08-13 | 2025-08-22 | 14 | CHI11-05-04-320: FS | CHI11-05-04-320
CHI11-05-04-330 | C05/04-L3Cx- FTE Energizations [480v] | 4 | 4 | 2025-08-23 | 2025-08-27 | 14 | CHI11-05-04-325: FS | CHI11-05-04-325
CHI11-05-04-335 | C05/04-L3Cx- Startups | 12 | 12 | 2025-08-28 | 2025-09-12 | 14 | CHI11-05-04-330: FS | CHI11-05-04-330
CHI11-05-04-340 | C05/04-L3Cx- Loadbanking | 4 | 4 | 2025-09-13 | 2025-09-17 | 14 | CHI11-05-02-340: FS, CHI11-05-04-335: FS | CHI11-05-02-340, CHI11-05-04-335
COLO 5 - CELL 3 |  | 39 | 39 | 2025-08-25 | 2025-10-11 | 0
CHI11-05-03-320 | C05/03-L3Cx- Control Power Checks | 8 | 8 | 2025-08-25 | 2025-09-03 | 0 | CHI11-05-03-315: SS 12 | CHI11-05-03-315
CHI11-05-03-325 | C05/03-L3Cx- EPMS Point to Point Checks | 8 | 8 | 2025-09-04 | 2025-09-13 | 0 | CHI11-05-03-320: FS | CHI11-05-03-320
CHI11-05-03-330 | C05/03-L3Cx- FTE Energizations [480v] | 5 | 5 | 2025-09-15 | 2025-09-19 | 0 | CHI11-05-03-325: FS | CHI11-05-03-325
CHI11-05-03-335 | C05/03-L3Cx- Startups | 12 | 12 | 2025-09-20 | 2025-10-04 | 0 | CHI11-05-03-330: FS | CHI11-05-03-330
CHI11-05-03-340 | C05/03-L3Cx- Loadbanking | 6 | 6 | 2025-10-06 | 2025-10-11 | 0 | CHI11-05-04-340: FS, CHI11-05-03-335: FS | CHI11-05-04-340, CHI11-05-03-335
Functional Testing (Level 4 & 5) |  | 27 | 27 | 2025-10-17 | 2025-11-19 | 0
CHI11-05-L4-10 | C05-L4Cx- Testing <MSFT Duration> | 24 | 24 | 2025-10-17 | 2025-11-15 | 0 | CHI11-04-L4-10: FS, CHI11-05-04-340: FS, CHI11-05-02-340: FS, CHI11-05-01-340: FS, CHI11-05-03-340: FS | CHI11-04-L4-10, CHI11-05-04-340, CHI11-05-02-340, CHI11-05-01-340, CHI11-05-03-340
CHI11-05-L5-10 | C05-L5Cx- Testing <MSFT Duration> | 3 | 3 | 2025-11-17 | 2025-11-19 | 0 | CHI11-05-L4-10: FS | CHI11-05-L4-10

## CFA - Fill Table
activity_id | activity_name | activity_code | color | trade | location | phase | start | sub_location | finish
Admin Area | [6 empty] | 20-Jan-25 |  | 09-May-25
Admin Gen Finishes & Punch | [6 empty] | 22-Feb-25 |  | 17-Mar-25
Admin/ COLO 3 | [6 empty] | 02-Sep-2024 |  | 02-Oct-25
Air Handling Units | [6 empty] | 09-Oct-2024 |  | 13-Mar-25
Auto Transfer Control Panel | [6 empty] | 08-Mar-25 |  | 08-Mar-25
Automatic Transfer Switches | [6 empty] | 15-Nov-24 |  | 23-Feb-25
Auxillary Power Distribution | [6 empty] | 08-Mar-25 |  | 08-Mar-25
BIM | [6 empty] | 18-Jul-2024 |  | 23-Dec-24
Beneficial Use Rooms | [6 empty] | 20-Jan-25 |  | 09-May-25
Beneficial Use/ TCO | [6 empty] | 14-Aug-25 |  | 02-Oct-25
Building Automation System | [6 empty] | 30-Nov-24 |  | 23-Feb-25
Busway / Busplugs | [6 empty] | 09-Apr-2024 |  | 23-Feb-25
CFCI (Critical Only) | [6 empty] | 07-Aug-2024 |  | 21-Nov-25
CHI-11-03-ADP-01 | Admin/C03- OFCI- Receive Auxillary (Mech) Power Distribution Panels (ADP) (Del Date- 3/8/2025) | [5 empty] | 08-Mar-2025
CHI-11-03-ADP-02 | Admin/C03- OFCI- Auxillary (Mech) Power Distribution Panels (ADP) Shipping/ ROJ | [5 empty] | 08-Mar-25 |  | 08-Mar-25
CHI-11-03-ADP-03 | Admin/C03- OFCI- Auxillary (Mech) Power Distribution Panels (ADP) Delivered | [7 empty] | 08-Mar-25
CHI-11-03-AHU-01 | Admin/C03- OFCI- Receive Air Handling Units (AHU) (Stulz) (SOW Del Date- 9/04/24) | [5 empty] | 09-Oct-2024
CHI-11-03-AHU-02 | Admin/C03- OFCI- Air Handling Units (AHU) (Stulz) Shipped/ROJ | [5 empty] | 09-Mar-25 |  | 13-Mar-25
CHI-11-03-AHU-03 | Admin/C03- OFCI- Air Handling Units (AHU) (Stulz) Delivered | [7 empty] | 13-Mar-25
CHI-11-03-ATS-01 | Admin/C03- OFCI- Receive Automatic Transfer Switches (ATS) (Schneider) (SOW Del Date- 4/30/24) | [5 empty] | 15-Nov-2024
CHI-11-03-ATS-02 | Admin/C03- OFCI- Automatic Transfer Switches (ATS) (Schneider) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-ATS-03 | Admin/C03- OFCI- Automatic Transfer Switches (ATS) (Schneider) Delivered | [7 empty] | 23-Feb-25
CHI-11-03-BAS-01 | Admin/C03- OFCI- Receive Building Automation System (BAS) (Automated Logic Corp) (SOW Del Date- 11/28/24) | [5 empty] | 30-Nov-2024
CHI-11-03-BAS-02 | Admin/C03- OFCI- Building Automation System (BAS) (ALC) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-BAS-03 | Admin/C03- OFCI- Building Automation System (BAS) (ALC) Delivered | [7 empty] | 23-Feb-25
CHI-11-03-BAS-F | Admin/COLO3- Complete BAS Testing | [7 empty] | 30-Aug-25
CHI-11-03-BFA-F | Admin/COLO3- Beneficial Use- Facilities Operations Center (FOC) | [7 empty] | 14-Aug-25
CHI-11-03-BFN-F | Admin/COLO3- Beneficial Use - All Facility & Network Telecom Access/ Devices etc. |  |  |  | ADMINCOLO3 |  |  |  | 01-Oct-2025
CHI-11-03-BND-F | Admin/COLO3- Beneficial Use (IDF#1,#2,#3 & #4) | [7 empty] | 14-Aug-25
CHI-11-03-BNF-F | Admin/COLO3- Beneficial Use - Facility Cable Room (FCR) |  |  |  | ADMINCOLO3 |  |  |  | 14-Aug-25
CHI-11-03-BNM-F | Admin/COLO3- Beneficial Use - Meet Me Room or Entry Rooms (MMR/ER) |  |  |  | ADMINCOLO3 |  |  |  | 14-Aug-25
CHI-11-03-BNS-F | Admin/COLO3- Beneficial Use - Security Equipment Room (SER) |  |  |  | ADMINCOLO3 |  |  |  | 14-Aug-25
CHI-11-03-BNU-F | Admin/COLO3- Beneficial Use | [7 empty] | 14-Aug-2025
CHI-11-03-BRN-F | Admin/COLO3- Beneficial Use- Regional Network Gateway (RNG) | [7 empty] | 14-Aug-25
CHI-11-03-BSA-F | Admin/COLO3- Beneficial Use- Security Operations Center (SOC) | [7 empty] | 14-Aug-25
CHI-11-03-BSC-F | Admin/COLO3- Beneficial Use - Security Corp Cable Rack (SCCR) Cabinets |  |  |  | ADMINCOLO3 |  |  |  | 14-Aug-25
CHI-11-03-BSHVS-F | Admin/COLO3- Beneficial Use - Secure & High Value Storage Rooms |  |  |  | ADMINCOLO3 |  |  |  | 14-Aug-25
CHI-11-03-BSL-F | Admin/COLO3- Beneficial Use- Security Low Voltage (SLV) System | [7 empty] | 14-Aug-25
CHI-11-03-BUS-01 | Admin/C03- OFCI- Receive Busway / Busplugs (Starline Holding) (Del Date- 1/25/24) | [5 empty] | 09-Apr-2024
CHI-11-03-BUS-02 | Admin/C03- OFCI- Busway / Busplugs (Starline Holding) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-BUS-03 | Admin/C03- OFCI- Busway / Busplugs (Starline Holding) Delivered | [7 empty] | 23-Feb-25
CHI-11-03-DAS-F | Admin/COLO3- Beneficial Use - Distributed Antenna System (DAS) |  |  |  | ADMINCOLO3 |  |  |  | 14-Aug-25
CHI-11-03-DRY-F | Admin/COLO3- Complete Weather Tight | [7 empty] | 16-Jan-2025
CHI-11-03-EPMS-01 | Admin/C03- OFCI- Receive Elec. Performance Monitoring System (EPMS) (Schneider) (SOW Del Date- 4/30/24) | [5 empty] | 15-Nov-2024
CHI-11-03-EPMS-02 | Admin/C03- OFCI- Elec. Performance Monitoring System (EPMS) (Schneider) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-EPMS-03 | Admin/C03- OFCI- Elec. Performance Monitoring System (EPMS) (Schneider) Delivered | [7 empty] | 23-Feb-25
CHI-11-03-EPMS-F | Admin/COLO3- Complete EPMS Testing | [7 empty] | 30-Aug-25
CHI-11-03-EW-F | GEN MS- Complete Earthwork & U/G Site Utilities | [7 empty] | 26-Dec-2024
CHI-11-03-EW-S | GEN MS- Earthworks & U/G Utilities Start | [5 empty] | 19-Aug-2024
CHI-11-03-FC-F | Admin/COLO3- Final Completion/ Turnover to Operations | [7 empty] | 02-Oct-2025
CHI-11-03-FIR-F | Admin/COLO3- Complete Fire Alarm | [7 empty] | 30-Aug-25
CHI-11-03-FITOUT-F | Admin/COLO- Admin & COLO3-5 Fitout Complete | [7 empty] | 01-Oct-2025
CHI-11-03-FND-F | Admin/COLO3- Complete Foundation | [7 empty] | 09-Oct-2024
CHI-11-03-FND-S | Admin/COLO3- Start Foundation | [5 empty] | 19-Sep-2024
CHI-11-03-GEN-01 | Admin/C03- OFCI- Receive Packaged Diesel Generator Set (CAT Holt) (SOW Del Date- 5/14/24) | [5 empty] | 15-Nov-2024
CHI-11-03-GEN-02 | Admin/C03- OFCI- Packaged Diesel Generator Set (CAT Holt) Shipping/ ROJ | [5 empty] | 20-Feb-25 |  | 24-Feb-25
CHI-11-03-GEN-03 | Admin/C03- OFCI- Packaged Diesel Generator Set (CAT Holt) Delivered | [7 empty] | 24-Feb-25
CHI-11-03-GEN-F | Admin/COLO3- Generator Ready for Fuel (Exterior Yard) | [7 empty] | 15-Mar-25
CHI-11-03-HAC-01 | Admin/C03- OFCI- Receive HAC/Racking (Tate Access) (SOW Del Date- 5/17/24) | [5 empty] | 15-Nov-2024
CHI-11-03-HAC-02 | Admin/C03- OFCI- HAC/Racking (Tate Access) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 21-Feb-25
CHI-11-03-HAC-03 | Admin/C03- OFCI- HAC/Racking (Tate Access) Delivered | [7 empty] | 21-Feb-25
CHI-11-03-L1CX-F | Admin/COLO3- Complete L1 Cx (All Red Tags/ ROJ) | [7 empty] | 04-Jun-25
CHI-11-03-L1CX-S | Admin/COLO3- Start L1 CX | [5 empty] | 09-Apr-25
CHI-11-03-L2CX-F | Admin/COLO3- Complete L2 Cx (Yellow Tag) | [7 empty] | 02-Jul-25
CHI-11-03-L2CX-S | Admin/COLO3- Start L2 CX (Yellow Tag) | [5 empty] | 05-May-25
CHI-11-03-L3CX-F | Admin/COLO3- Complete CX L3 (Green Tag) | [7 empty] | 14-Aug-2025
CHI-11-03-L3CX-S | Admin/COLO3- Start L3 CX (Green Tag) | [5 empty] | 04-Jun-25
CHI-11-03-L4CX-F | Admin/COLO3- Complete L4 Cx (Blue Tag) | [7 empty] | 15-Sep-25
CHI-11-03-L4CX-S | Admin/COLO3- Start L4 Cx (Blue Tag) | [5 empty] | 15-Aug-25
CHI-11-03-L5CX-F | Admin/COLO3- Cx L5 IST Complete (White Tag) | [7 empty] | 18-Sep-2025
CHI-11-03-L5CX-S | Admin/COLO3- Start L5 Cx (White Tag) | [5 empty] | 16-Sep-25
CHI-11-03-LHP-F | GEN MS- Complete Landscaping/ Hardscaping | [7 empty] | 19-Nov-25
CHI-11-03-LVS-01 | Admin/C03- OFCI- Receive LV Switchgear (LVS) (Eaton) (SOW Del Date- 2/28/25) | [5 empty] | 28-Feb-2025
CHI-11-03-LVS-02 | Admin/C03- OFCI- LV Switchgear (LVS) (Eaton) Shipping/ ROJ | [5 empty] | 28-Feb-25 |  | 04-Mar-25
CHI-11-03-LVS-03 | Admin/C03- OFCI- LV Switchgear (LVS) (Eaton) Delivered | [7 empty] | 04-Mar-25
CHI-11-03-MOB-F | GEN MS- GC Mobilization Finish/ Site Secured | [7 empty] | 16-Sep-2024
CHI-11-03-MOB-S | GEN MS- GC Mobilization Start | [5 empty] | 24-Jul-2024
CHI-11-03-MOR-F | Admin/COLO3- Beneficial Use - Middle of Row (MOR) Cabinets |  |  |  | ADMINCOLO3 |  |  |  | 14-Aug-25
CHI-11-03-MSB-01 | Admin/C03- OFCI- Receive Main LV Switch Board (MSB) (SOW Del Date- 3/8/2025) | [5 empty] | 08-Mar-2025
CHI-11-03-MSB-02 | Admin/C03- OFCI- Main LV Switch Board (MSB) Shipping/ ROJ | [5 empty] | 08-Mar-25 |  | 08-Mar-25
CHI-11-03-MSB-03 | Admin/C03- OFCI- Main LV Switch Board (MSB) Delivered | [7 empty] | 08-Mar-25
CHI-11-03-MVS-01 | Admin/C03- OFCI- Receive Medium Voltage Switchgear (JDC Power Sys) (SOW Del Date- 7/30/24) | [5 empty] | 15-Oct-2024
CHI-11-03-MVS-02 | Admin/C03- OFCI- Medium Voltage Switchgear (MVS) (JD Power Sys) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-MVS-03 | Admin/C03- OFCI- Medium Voltage Switchgear (MVS) (JD Power Sys) Delivered | [7 empty] | 23-Feb-25
CHI-11-03-P1ST-F | Admin/COLO3- Phase 1 Security Pre-Testing Complete | [7 empty] | 30-Aug-2025
CHI-11-03-P2ST-F | Admin/COLO3- Phase 2 Security Pre-Testing Complete | [7 empty] | 04-Sep-2025
CHI-11-03-P3ST-F | Admin/COLO3- Phase 3 Security Pre-Testing Complete | [7 empty] | 25-Sep-2025
CHI-11-03-PAD-F | GEN MS- Building Footprint Pad Ready | [7 empty] | 04-Sep-2024
CHI-11-03-PDU-01 | Admin/C03- OFCI- Receive Power Distribution Units (PDU) (ABB) (SOW Del Date- 4/30/24) | [5 empty] | 15-Nov-2024
CHI-11-03-PDU-02 | Admin/C03- OFCI- Power Distribution Units (PDU) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-PDU-03 | Admin/C03- OFCI- Power Distribution Units (PDU) Delivered | [7 empty] | 23-Feb-25
CHI-11-03-PEMB-01 | Admin/C03-5- OFCI- Receive PEMB Procurement (1st Del) (Nucor) (SOW Del Date-10/3/24) | [5 empty] | 14-Oct-2024
CHI-11-03-PEMB-02 | Admin/C03-5- OFCI- PEMB Procurement (1st Del) (Nucor) Shipping/ ROJ | [5 empty] | 14-Oct-2024 |  | 14-Oct-2024
CHI-11-03-PEMB-03 | Admin/C03-5- OFCI- PEMB Procurement (1st Del) (Nucor) Delivered | [7 empty] | 14-Oct-2024
CHI-11-03-POW-F | Admin/COLO3- Complete Utility Power- On | [7 empty] | 05-May-25
CHI-11-03-PROP-F | GEN MS- Clayco Proposal Due date | [7 empty] | 12-Apr-2024
CHI-11-03-PSR-F | GEN MS- PSR (Contract) Executed | [7 empty] | 30-Sep-2024
CHI-11-03-RNI-F | Admin/COLO3- RNI | [7 empty] | 20-Aug-2025
CHI-11-03-ROJ-F | Admin/COLO3- Complete Last ROJ | [7 empty] | 08-Mar-25
CHI-11-03-ROJ-S | Admin/COLO3- Start First ROJ CLAYCO Took over Storage 9/2/2024 | [5 empty] | 02-Sep-2024
CHI-11-03-RoIP-F | Admin/COLO3- Beneficial Use - Radio Over Internet Protocol (RoIP) |  |  |  | ADMINCOLO3 |  |  |  | 14-Aug-25
CHI-11-03-SC-F | Admin/COLO3- Substantial Completion | [7 empty] | 01-Oct-25
CHI-11-03-SL-F | Admin/COLO3- Security Lockdown | [7 empty] | 02-Oct-2025
CHI-11-03-SOG-F | Admin/COLO3- Complete SOG | [7 empty] | 27-Dec-24
CHI-11-03-SUP-F | Admin/COLO3- Complete Superstructure | [7 empty] | 14-Dec-24
CHI-11-03-SUP-S | Admin/COLO3- Start Superstructure | [5 empty] | 14-Oct-2024
CHI-11-03-TCO-F | Admin/COLO3- TCO / C of O |  |  |  | COLO3TCO |  |  |  | 30-Sep-2025
CHI-11-03-TCP-01 | Admin/C03- OFCI- Receive Auto Transfer Control Panel (TCP) (Del Date- 3/8/2025) | [5 empty] | 08-Mar-2025
CHI-11-03-TCP-02 | Admin/C03- OFCI- Auto Transfer Control Panel (TCP) Shipping/ ROJ | [5 empty] | 08-Mar-25 |  | 08-Mar-25
CHI-11-03-TCP-03 | Admin/C03- OFCI- Auto Transfer Control Panel (TCP) Delivered | [7 empty] | 08-Mar-25
CHI-11-03-UGE-F | Admin/COLO3- Complete U/G Utilities/ MV UG Electrical | [7 empty] | 14-Dec-24
CHI-11-03-UGU-F | Admin/COLO3- Complete U/G Utilities (No Elec) | [7 empty] | 14-Dec-24
CHI-11-03-UPM-01 | Admin/C03- OFCI- Receive Utility Pad Mount Switchgear (Del Date- 7/30/2024) | [5 empty] | 23-Oct-2024
CHI-11-03-UPM-02 | Admin/C03- OFCI- Utility Pad Mount Switchgear (UPM) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-UPM-03 | Admin/C03- OFCI- Utility Pad Mount Switchgear (UPM) Delivered | [5 empty] | 24-Feb-25 |  | 28-Feb-25
CHI-11-03-UPS-01 | Admin/C03- OFCI- Received SUB Warehouse 9/28/2023 UPS System w/ Battery (UPS) (Eaton) (SOW Del Date- 8/13/23) | [5 empty] | 02-Sep-2024
CHI-11-03-UPS-02 | Admin/C03- OFCI- UPS System w/ Battery (UPS) (Eaton) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-UPS-03 | Admin/C03- OFCI- UPS System w/ Battery (UPS) (Eaton) Delivered | [7 empty] | 23-Feb-25
CHI-11-03-XFM-01 | Admin/C03- OFCI- Receive Pad Mounted Transformers (XFM-TX) (Del Date- 7/30/2024) | [5 empty] | 15-Nov-2024
CHI-11-03-XFM-02 | Admin/C03- OFCI- Pad Mounted Transformers (XFM-TX) Shipping/ ROJ | [5 empty] | 19-Feb-25 |  | 23-Feb-25
CHI-11-03-XFM-03 | Admin/C03- OFCI- Pad Mounted Transformers (XFM-TX) Delivered | [7 empty] | 23-Feb-25
CHI-11-04-ADP-01 | C04- OFCI- Receive Mech Power Distribution Panels (ADP) (Del Date 3/30/2025) | [5 empty] | 30-Mar-2025
CHI-11-04-ADP-02 | C04- OFCI- Mech Power Distribution Panels (ADP) Shipping/ROJ | [5 empty] | 30-Mar-25 |  | 30-Mar-25
CHI-11-04-ADP-03 | C04- OFCI- Mech Power Distribution Panels (ADP) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-AHU-01 | C04- OFCI- Receive Air Handling Units (AHU) (Stulz) (SOW Del Date- 9/9/24) | [5 empty] | 30-Sep-2024
CHI-11-04-AHU-02 | C04- OFCI- Air Handling Units (AHU) (Stulz) Shipping/ ROJ | [5 empty] | 01-Apr-25 |  | 05-Apr-25
CHI-11-04-AHU-03 | C04- OFCI- Air Handling Units (AHU) (Stulz) Delivered | [7 empty] | 05-Apr-25
CHI-11-04-ATS-01 | C04- OFCI- Receive Automatic Transfer Switches (ATS) (Schneider) (SOW Del Date- 6/30/24) | [5 empty] | 15-Nov-24
CHI-11-04-ATS-02 | C04- OFCI- Automatic Transfer Switches (ATS) (Schneider) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-04-ATS-03 | C04- OFCI- Automatic Transfer Switches (ATS) (Schneider) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-BAS-01 | C04- OFCI- Receive Building Automation System (BAS) (Automated Logic Corp) (SOW Del Date- 12/29/24) | [5 empty] | 29-Dec-2024
CHI-11-04-BAS-02 | C04- OFCI- Building Automation System (BAS) (Automated Logic Corp) Shipping/ROJ | [5 empty] | 29-Dec-24 |  | 04-Jan-25
CHI-11-04-BAS-03 | C04- OFCI- Building Automation System (BAS) (Automated Logic Corp) Delivered | [7 empty] | 04-Jan-25
CHI-11-04-BAS-F | COLO4- Complete BAS Testing | [7 empty] | 30-Sep-25
CHI-11-04-BFA-F | COLO4- Beneficial Use- Facilities Operations Center (FOC) | [7 empty] | 19-Sep-25
CHI-11-04-BND-F | COLO4- Beneficial Use- (IDF#1,#2,#3 & #4) | [7 empty] | 19-Sep-25
CHI-11-04-BNF-F | COLO4- Beneficial Use- Facility Cable Room (FCR) | [7 empty] | 19-Sep-25
CHI-11-04-BNM-F | COLO4- Beneficial Use- Meet Me Room or Entry Rooms (MMR/ER) | [7 empty] | 19-Sep-25
CHI-11-04-BNU-F | COLO4- Beneficial Use | [7 empty] | 19-Sep-2025
CHI-11-04-BSC-F | COLO4- Beneficial Use - Security Corp Cable Rack (SCCR) Cabinets |  |  |  | COLO4 |  |  |  | 19-Sep-25
CHI-11-04-BSHVS-F | COLO4- Beneficial Use- Secure & High Value Storage Rooms | [7 empty] | 19-Sep-25
CHI-11-04-BSL-F | COLO4- Beneficial Use - Security Low Voltage (SLV) Systems |  |  |  | COLO4 |  |  |  | 19-Sep-25
CHI-11-04-BUS-01 | C04- OFCI- Receive Busway / Busplugs (BSW) (Starline Holding) (SOW Del Date- 2/23/24) | [5 empty] | 15-Nov-2024
CHI-11-04-BUS-02 | C04- OFCI- Busway / Busplugs (BSW) (Starline Holding) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-04-BUS-03 | C04- OFCI- Busway / Busplugs (BSW) (Starline Holding) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-DAS-F | COLO4- Beneficial Use - Distrbuted Antenna System (DAS) |  |  |  | COLO4 |  |  |  | 19-Sep-25
CHI-11-04-DRY-F | COLO4- Weather Tight | [5 empty] | 30-Jan-25 |  | 30-Jan-25
CHI-11-04-EPMS-01 | C04- OFCI- Receive Elec. Performance Monitoring Syst. (EPMS) (EPMS) (Schneider) (SOW Del Date- 6/30/24) | [5 empty] | 15-Nov-2024
CHI-11-04-EPMS-02 | C04- OFCI- Elec. Performance Monitoring Syst. (EPMS) (EPMS) (Schneider) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-04-EPMS-03 | C04- OFCI- Elec. Performance Monitoring Syst. (EPMS) (EPMS) (Schneider) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-EPMS-F | COLO4- Complete EPMS Testing | [7 empty] | 30-Sep-25
CHI-11-04-FC-F | COLO4- Final Completion/ Turnover to Operations | [7 empty] | 06-Nov-2025
CHI-11-04-FIR-F | COLO4- Complete Fire Alarm | [7 empty] | 30-Sep-25
CHI-11-04-FND-F | COLO4- Complete Foundation | [7 empty] | 31-Oct-2024
CHI-11-04-FND-S | COLO4- Foundation Start | [5 empty] | 19-Sep-2024
CHI-11-04-GEN-01 | C04- OFCI- Receive Packaged Diesel Generator Set (GEN) (CAT Holt) (SOW Del Date- 6/4/24) | [5 empty] | 15-Nov-2024
CHI-11-04-GEN-02 | C04- OFCI- Packaged Diesel Generator Set (GEN) (CAT Holt) Shipping/ROJ | [5 empty] | 06-Apr-25 |  | 10-Apr-25
CHI-11-04-GEN-03 | C04- OFCI- Packaged Diesel Generator Set (GEN) (CAT Holt) Delivered | [7 empty] | 10-Apr-25
CHI-11-04-GEN-F | COLO4- Generator Ready for Fuel | [7 empty] | 24-Apr-25
CHI-11-04-HAC-01 | C04- OFCI- Receive HAC/Racking (Tate Access) (SOW Del Date- 6/18/24) | [5 empty] | 15-Nov-2024
CHI-11-04-HAC-02 | C04- OFCI- HAC/Racking (Tate Access) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 28-Mar-25
CHI-11-04-HAC-03 | C04- OFCI- HAC/Racking (Tate Access) Delivered | [7 empty] | 28-Mar-25
CHI-11-04-L1CX-F | COLO4- Complete L1 Cx (All Red Tags/ ROJ) | [7 empty] | 19-Jul-25
CHI-11-04-L1CX-S | COLO4- Start L1 CX | [5 empty] | 23-Apr-25
CHI-11-04-L2CX-F | COLO4- Complete L2 Cx (Yellow Tag) | [7 empty] | 14-Aug-25
CHI-11-04-L2CX-S | COLO4- Start L2 CX (Yellow Tag) | [5 empty] | 06-May-25
CHI-11-04-L3CX-S | COLO4- Start L3 CX | [5 empty] | 20-Jun-25
CHI-11-04-L3Cx-F | COLO4- CX L3 Complete | [7 empty] | 19-Sep-2025
CHI-11-04-L4CX-F | COLO4- Complete L4 Cx (Blue Tag) | [7 empty] | 16-Oct-25
CHI-11-04-L4CX-S | COLO4- Start L4 Cx (Blue Tag) | [5 empty] | 20-Sep-25
CHI-11-04-L5CX-S | COLO4- Start L5 Cx (White Tag) | [5 empty] | 17-Oct-25
CHI-11-04-L5Cx-F | COLO4- Cx L5 IST Complete | [7 empty] | 20-Oct-2025
CHI-11-04-LVS-01 | C04- OFCI- Receive LV Switchgear (Eaton) (SOW Del Date- 2/28/25) | [5 empty] | 28-Feb-2025
CHI-11-04-LVS-02 | C04- OFCI- LV Switchgear (Eaton) Shipping/ROJ | [5 empty] | 28-Feb-25 |  | 02-Mar-25
CHI-11-04-LVS-03 | C04- OFCI- LV Switchgear (Eaton) Delivered | [7 empty] | 02-Mar-25
CHI-11-04-MOR-F | COLO4- Beneficial Use- Middle of Row (MOR) Cabinets | [7 empty] | 19-Sep-25
CHI-11-04-MSB-01 | C04- OFCI- Receive Main LV Switch Board (MSB) (Del Date 3/30/2025) | [5 empty] | 30-Mar-2025
CHI-11-04-MSB-02 | C04- OFCI- Main LV Switch Board (MSB) Shipping/ROJ | [5 empty] | 30-Mar-25 |  | 30-Mar-25
CHI-11-04-MSB-03 | C04- OFCI- Main LV Switch Board (MSB) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-MVS-01 | C04- OFCI- Receive Medium Voltage Switchgear (JDC Power Sys) (SOW Del Date- 8/30/24) | [5 empty] | 23-Oct-2024
CHI-11-04-MVS-02 | C04- OFCI- Medium Voltage Switchgear (JDC Power Sys) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-04-MVS-03 | C04- OFCI- Medium Voltage Switchgear (JDC Power Sys) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-P1ST-F | COLO4- Phase 1 Security Pre-Testing Complete | [7 empty] | 30-Sep-2025
CHI-11-04-P2ST-F | COLO4- Phase 2 Security Pre-Testing Complete | [7 empty] | 04-Oct-2025
CHI-11-04-P3ST-F | COLO4- Phase 3 Security Pre-Testing Complete | [7 empty] | 23-Oct-2025
CHI-11-04-PDU-01 | C04- OFCI- Reveive Power Distribution Units (PDU) (ABB) (SOW Del Date- 7/12/24) | [5 empty] | 15-Nov-2024
CHI-11-04-PDU-02 | C04- OFCI- Power Distribution Units (PDU) (ABB) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-04-PDU-03 | C04- OFCI- Power Distribution Units (PDU) (ABB) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-POW-F | COLO4- Complete Utility Power- On | [7 empty] | 05-May-25
CHI-11-04-RNI-F | COLO4- Ready for Network Install | [7 empty] | 24-Sep-2025
CHI-11-04-ROJ-F | COLO4- Complete Last ROJ | [7 empty] | 30-Mar-25
CHI-11-04-ROJ-S | COLO4- Start First ROJ CLAYCO Took over Storage 9/2/2024 | [5 empty] | 02-Sep-2024
CHI-11-04-RoIP-F | COLO4- Beneficial Use- Radio OVer Internet Protocol (RoIP) | [7 empty] | 19-Sep-25
CHI-11-04-SC-F | COLO4- Substantial Completion | [7 empty] | 29-Oct-25
CHI-11-04-SL-F | COLO4- Security Lockdown | [7 empty] | 06-Nov-2025
CHI-11-04-SOG-F | COLO4- Complete SOG | [7 empty] | 10-Jan-25
CHI-11-04-SUP-F | COLO4- Complete Superstructure | [7 empty] | 31-Dec-24
CHI-11-04-SUP-S | COLO4- Start Superstructure | [5 empty] | 01-Nov-2024
CHI-11-04-TCO-F | COLO4- TCO / C of O |  |  |  | COLO4TCO |  |  |  | 29-Oct-2025
CHI-11-04-TCP-01 | C04- OFCI- Receive Auto Transfer Control Panel (TCP) (Del Date-3/30/2025) | [5 empty] | 30-Mar-2025
CHI-11-04-TCP-02 | C04- OFCI- Auto Transfer Control Panel (TCP) Shipping/ROJ | [5 empty] | 30-Mar-25 |  | 30-Mar-25
CHI-11-04-TCP-03 | C04- OFCI- Auto Transfer Control Panel (TCP) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-UGE-F | COLO4- Complete U/G Utilities/ MV UG Electric | [7 empty] | 27-Dec-24
CHI-11-04-UPM-01 | C04- OFCI- Receive Utility Pad Mount Switchgear (UPM) (Del Date 8/30/2024) | [5 empty] | 23-Oct-2024
CHI-11-04-UPM-02 | C04- OFCI- Utility Pad Mount Switchgear (UPM) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-04-UPM-03 | C04- OFCI- Utility Pad Mount Switchgear (UPM) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-UPS-01 | C04- OFCI- Received SUB Warehouse 11/23/2023 Static UPS System W/Batt (UPS) (Eaton) (SOW Del Date- 11/11/23) | [5 empty] | 02-Sep-2024
CHI-11-04-UPS-02 | C04- OFCI- Static UPS System W/Batt (UPS) (Eaton) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-04-UPS-03 | C04- OFCI- Static UPS System W/Batt (UPS) (Eaton) Delivered | [7 empty] | 30-Mar-25
CHI-11-04-XFM-01 | C04- OFCI- Reveive Pad Mounted Transformers (XMF) (Del Date 8/30/2024) | [5 empty] | 15-Nov-2024
CHI-11-04-XFM-02 | C04- OFCI- Pad Mounted Transformers (XMF) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-04-XFM-03 | C04- OFCI- Pad Mounted Transformers (XMF) Delivered | [7 empty] | 30-Mar-25
CHI-11-05-ADP-01 | C05- OFCI- Receive Mech Power Distribution Panels (ADP) (Del Date 3/30/2025) | [5 empty] | 30-Mar-2025
CHI-11-05-ADP-02 | C05- OFCI- Mech Power Distribution Panels (ADP) Shipping/ROJ | [5 empty] | 30-Mar-25 |  | 04-Apr-25
CHI-11-05-ADP-03 | C05- OFCI- Mech Power Distribution Panels (ADP) Delivered | [7 empty] | 04-Apr-25
CHI-11-05-AHU-01 | C05- OFCI- Receive Air Handling Units (AHU) (Stulz) (SOW Del Date- 9/16/24) | [5 empty] | 12-Sep-2024
CHI-11-05-AHU-02 | C05- OFCI- Air Handling Units (AHU) (Stulz) Shipping/ROJ | [5 empty] | 11-May-25 |  | 11-May-25
CHI-11-05-AHU-03 | C05- OFCI- Air Handling Units (AHU) (Stulz) Delivered | [7 empty] | 11-May-25
CHI-11-05-ATS-01 | C05- OFCI- Receive Automatic Transfer Switches (ATS) (Schneider) (SOW Del Date- 8/31/24) | [5 empty] | 15-Nov-2024
CHI-11-05-ATS-02 | C05- OFCI- Automatic Transfer Switches (ATS) (Schneider) Shipping/ROJ | [5 empty] | 20-Apr-25 |  | 20-Apr-25
CHI-11-05-ATS-03 | C05- OFCI- Automatic Transfer Switches (ATS) (Schneider) Delivered | [7 empty] | 20-Apr-25
CHI-11-05-BAS-01 | C05- OFCI- Receive Building Automation System (BAS) (Automated Logic Corp) (SOW Del Date- 1/28/25) | [5 empty] | 28-Jan-2025
CHI-11-05-BAS-02 | C05- OFCI- Building Automation System (BAS) (Automated Logic Corp) Shipping/ROJ | [5 empty] | 28-Jan-25 |  | 02-Feb-25
CHI-11-05-BAS-03 | C05- OFCI- Building Automation System (BAS) (Automated Logic Corp) Delivered | [7 empty] | 02-Feb-25
CHI-11-05-BAS-F | COLO5- Complete BAS Testing | [7 empty] | 31-Oct-25
CHI-11-05-BMOR-F | COLO5- Beneficial Use- Middle of Row (MOR) Cabinets | [7 empty] | 11-Oct-25
CHI-11-05-BND-F | COLO5- Beneficial Use (IDF#1,#2,#3 & #4) | [7 empty] | 11-Oct-25
CHI-11-05-BNF-F | COLO5- Beneficial Use Facility Cable Room (FCR) | [7 empty] | 11-Oct-25
CHI-11-05-BNM-F | COLO5- Beneficial Use Meet Me Room or Entry Rooms (MMR/ER) | [7 empty] | 11-Oct-25
CHI-11-05-BNU-F | COLO5- Beneficial Use | [7 empty] | 11-Oct-2025
CHI-11-05-BSC-F | COLO5- Beneficial Use - Security Corp Cable Rack (SCCR) Cabinets |  |  |  | COLO5 |  |  |  | 11-Oct-25
CHI-11-05-BSHVS-F | COLO5- Beneficial Use Secure & High Value Storage Rooms | [7 empty] | 11-Oct-25
CHI-11-05-BSL-F | COLO5- Beneficial Use - Security Low Voltage (SLV) System |  |  |  | COLO5 |  |  |  | 11-Oct-25
CHI-11-05-BUS-01 | C05- OFCI- Receive Busway / Busplugs (BSW) (Starline Holding) (SOW Del Date- 4/23/24) | [5 empty] | 15-Nov-2024
CHI-11-05-BUS-02 | C05- OFCI- Busway / Busplugs (BSW) (Starline Holding) Shipping/ROJ | [5 empty] | 29-Apr-25 |  | 03-May-25
CHI-11-05-BUS-03 | C05- OFCI- Busway / Busplugs (BSW) (Starline Holding) Delivered | [7 empty] | 03-May-25
CHI-11-05-DAS-F | COLO5- Beneficial Use - Distributed Antenna System (DAS) |  |  |  | COLO5 |  |  |  | 11-Oct-25
CHI-11-05-DRY-F | Weather Tight - Entire Building | [7 empty] | 14-Feb-25
CHI-11-05-EPMS-01 | C05- OFCI- Receive Elec. Performance Monitoring Syst. (EPMS) (Schneider) (SOW Del Date- 8/31/24) | [5 empty] | 15-Nov-2024
CHI-11-05-EPMS-02 | C05- OFCI- Elec. Performance Monitoring Syst. (EPMS) (Schneider) Shipping/ROJ | [5 empty] | 20-Apr-25 |  | 20-Apr-25
CHI-11-05-EPMS-03 | C05- OFCI- Elec. Performance Monitoring Syst. (EPMS) (Schneider) Delivered | [7 empty] | 20-Apr-25
CHI-11-05-EPMS-F | COLO5- Complete EPMS Testing | [7 empty] | 31-Oct-25
CHI-11-05-FC-F | COLO5- Final Completion/Turnover to Operations | [7 empty] | 04-Dec-2025
CHI-11-05-FIR-F | COLO5- Complete Fire Alarm | [7 empty] | 31-Oct-25
CHI-11-05-FND-F | COLO5- Complete Foundation | [7 empty] | 12-Nov-2024
CHI-11-05-FND-S | COLO5- Foundation Start | [5 empty] | 19-Sep-2024
CHI-11-05-GEN-01 | C05- OFCI- Receive Packaged Diesel Generator Set (GPC) (CAT Holt) (SOW Del Date- 6/26/24) | [5 empty] | 15-Nov-2024
CHI-11-05-GEN-02 | C05- OFCI- Packaged Diesel Generator Set (GPC) (CAT Holt) Shipping/ROJ | [5 empty] | 11-May-25 |  | 15-May-25
CHI-11-05-GEN-03 | C05- OFCI- Packaged Diesel Generator Set (GPC) (CAT Holt) Delivered | [7 empty] | 15-May-25
CHI-11-05-GEN-F | COLO5- Generator Ready for Fuel | [7 empty] | 31-May-25
CHI-11-05-HAC-01 | C05- OFCI- Receive HAC/Racking (Tate Access) (SOW Del Date- 7/3/24) | [5 empty] | 15-Nov-2024
CHI-11-05-HAC-02 | C05- OFCI- HAC/Racking (Tate Access) Shipping/ROJ | [5 empty] | 25-Apr-25 |  | 28-Apr-25
CHI-11-05-HAC-03 | C05- OFCI- HAC/Racking (Tate Access) Delivered | [7 empty] | 28-Apr-25
CHI-11-05-L1CX-F | COLO5- Complete L1 Cx (All Red Tags/ ROJ) | [7 empty] | 05-Aug-25
CHI-11-05-L1CX-S | COLO5- Start L1 CX | [5 empty] | 21-Apr-25
CHI-11-05-L2CX-F | COLO5- Complete L2 Cx (Yellow Tag) | [7 empty] | 03-Sep-25
CHI-11-05-L2CX-S | COLO5- Start L2 CX (Yellow Tag) | [5 empty] | 05-Jun-25
CHI-11-05-L3CX-F | COLO5- CX Level 3 Complete | [7 empty] | 11-Oct-2025
CHI-11-05-L3CX-S | COLO5- Start L3 CX | [5 empty] | 19-Jul-25
CHI-11-05-L4CX-F | COLO5- Complete L4 Cx (Blue Tag) | [7 empty] | 15-Nov-25
CHI-11-05-L4CX-S | COLO5- Start L4 Cx (Blue Tag) | [5 empty] | 17-Oct-25
CHI-11-05-L5CX-F | COLO5- Cx Level 5 IST Complete | [7 empty] | 19-Nov-2025
CHI-11-05-L5CX-S | COLO5- Start L5 Cx (White Tag) | [5 empty] | 17-Nov-25
CHI-11-05-LVS-01 | C05- OFCI- Receive LV Switchgear (Eaton) (SOW Del Date- 3/30/25) | [5 empty] | 30-Mar-2025
CHI-11-05-LVS-02 | C05- OFCI- LV Switchgear (Eaton) Shipping/ROJ | [5 empty] | 30-Mar-25 |  | 03-Apr-25
CHI-11-05-LVS-03 | C05- OFCI- LV Switchgear (Eaton) Delivered | [7 empty] | 03-Apr-25
CHI-11-05-MSB-01 | C05- OFCI- Receive Main LV Switch Board (MSB) (Del Date 3/30/2025) | [5 empty] | 30-Mar-2025
CHI-11-05-MSB-02 | C05- OFCI- Main LV Switch Board (MSB) Shipping/ROJ | [5 empty] | 30-Mar-25 |  | 04-Apr-25
CHI-11-05-MSB-03 | C05- OFCI- Main LV Switch Board (MSB) Delivered | [7 empty] | 04-Apr-25
CHI-11-05-MVS-01 | C05- OFCI- Receive Medium Voltage Switchgear (MVS) (JDC Power Sys) (SOW Del Date- 10/30/24) | [5 empty] | 30-Oct-2024
CHI-11-05-MVS-02 | C05- OFCI- Medium Voltage Switchgear (MVS) (JDC Power Sys) Shipping/ROJ | [5 empty] | 29-Apr-25 |  | 03-May-25
CHI-11-05-MVS-03 | C05- OFCI- Medium Voltage Switchgear (MVS) (JDC Power Sys) Delivered | [7 empty] | 03-May-25
CHI-11-05-P1ST-F | COLO5- Phase 1 Security Pre-Testing Complete | [7 empty] | 31-Oct-2025
CHI-11-05-P2ST-F | COLO5- Phase 2 Security Pre-Testing Complete | [7 empty] | 03-Nov-2025
CHI-11-05-P3ST-F | COLO5- Phase 3 Security Pre-Testing Complete | [7 empty] | 26-Nov-2025
CHI-11-05-PDU-01 | C05- OFCI- Receive Power Distribution Units (PDU) (ABB) (SOW Del Date- 9/30/24) | [5 empty] | 15-Nov-2024
CHI-11-05-PDU-02 | C05- OFCI- Power Distribution Units (PDU) (ABB) Shipping/ROJ | [5 empty] | 03-May-25 |  | 07-May-25
CHI-11-05-PDU-03 | C05- OFCI- Power Distribution Units (PDU) (ABB) Delivered | [7 empty] | 07-May-25
CHI-11-05-POW-F | COLO5- Complete Utility Power- On | [7 empty] | 05-May-25
CHI-11-05-RNI-F | COLO5- Ready for Network Install | [7 empty] | 17-Oct-2025
CHI-11-05-ROJ-F | COLO5- Complete Last ROJ | [7 empty] | 31-Mar-25
CHI-11-05-ROJ-S | COLO5- Start First ROJ - CLAYCO Took over Storage 9/2/2024 |  |  |  | COLO5 |  | 02-Sep-2024
CHI-11-05-RoIP-F | COLO5- Beneficial Use- Radio Over Internet Protocol (RoIP) | [7 empty] | 11-Oct-25
CHI-11-05-SC-F | COLO5- Substantial Completion | [7 empty] | 02-Dec-25
CHI-11-05-SL-F | COLO5- Secuirty Lockdown | [7 empty] | 04-Dec-2025
CHI-11-05-SOG-F | COLO5- Complete SOG | [7 empty] | 25-Jan-25
CHI-11-05-SUP-F | COLO5- Complete Superstructure | [7 empty] | 15-Jan-25
CHI-11-05-SUP-S | COLO5- Start Superstructure | [5 empty] | 12-Nov-2024
CHI-11-05-TCO-F | COLO5- TCO / C of O |  |  |  | COLO5TCO |  |  |  | 02-Dec-2025
CHI-11-05-TCP-01 | C05- OFCI- Receive Auto Transfer Control Panel (TCP) (Del Date 3/30/2025) | [5 empty] | 30-Mar-2025
CHI-11-05-TCP-02 | C05- OFCI- Auto Transfer Control Panel (TCP) Shipping/ROJ | [5 empty] | 30-Mar-25 |  | 04-Apr-25
CHI-11-05-TCP-03 | C05- OFCI- Auto Transfer Control Panel (TCP) Delivered | [7 empty] | 04-Apr-25
CHI-11-05-UGE-F | COLO5- Complete U/G Utilities/ MV UG Electric | [7 empty] | 13-Jan-25
CHI-11-05-UPM-01 | C05- OFCI- Receive Utility Pad Mount Switchgear (UPM) (Del Date 10/30/2024) | [5 empty] | 23-Oct-2024
CHI-11-05-UPM-02 | C05- OFCI- Utility Pad Mount Switchgear (UPM) Shipping/ROJ | [5 empty] | 29-Apr-25 |  | 03-May-25
CHI-11-05-UPM-03 | C05- OFCI- Utility Pad Mount Switchgear (UPM) Delivered | [7 empty] | 03-May-25
CHI-11-05-UPS-01 | C05- OFCI- Received SUB Warehouse 12/28/2023 Static UPS System W/Batt (UPS) (Eaton) (SOW Del Date- 12/11/23) | [5 empty] | 02-Sep-2024
CHI-11-05-UPS-02 | C05- OFCI- Static UPS System W/Batt (UPS) (Eaton) Shipping/ROJ | [5 empty] | 26-Mar-25 |  | 30-Mar-25
CHI-11-05-UPS-03 | C05- OFCI- Static UPS System W/Batt (UPS) (Eaton) Delivered | [7 empty] | 30-Mar-25
CHI-11-05-XFM-01 | C05- OFCI- Receive Pad Mounted Transformers (XMF) (Del Date 10/30/2024) | [5 empty] | 15-Nov-2024
CHI-11-05-XFM-02 | C05- OFCI- Pad Mounted Transformers (XMF) Shipping/ROJ | [5 empty] | 29-Apr-25 |  | 03-May-25
CHI-11-05-XFM-03 | C05- OFCI- Pad Mounted Transformers (XMF) Delivered | [7 empty] | 03-May-25
CHI-11-CFCI-10 | CFCI- MV Metering Cabinet - Substitute [43 Weeks] | [5 empty] | 07-Aug-2024 |  | 18-Jun-25
CHI-11-CFCI-15 | CFCI- MV Metering Cabinet - *Not Used* [65 Weeks] - Not Tied | [5 empty] | 07-Aug-2024 |  | 21-Nov-25
CHI-11-CFCI-20 | CFCI- MV Cables Fabrication/ Lead Time | [5 empty] | 17-Aug-2024 |  | 24-Apr-25
CHI-11-CFCI-25 | CFCI- Cable Bus Fabrication/ Lead Time | [5 empty] | 15-Nov-24 |  | 03-Mar-25
CHI-11-CFCI-30 | CFCI- HACs Fabrication/ Lead Time | [5 empty] | 15-Nov-24 |  | 05-Dec-24
CHI-11-MS-01 | CHI11: Construction Start | [5 empty] | 19-Aug-2024
CHI-11-MS-02 | CHI11: Building Pad Ready | [7 empty] | 04-Sep-2024
CHI-11-MS-03 | CHI11: Foundations Complete | [7 empty] | 12-Nov-2024
CHI-11-MS-04 | CHI11: Structure Start | [5 empty] | 14-Oct-2024
CHI-11-MS-05 | CHI11: Structure Complete | [7 empty] | 03-Dec-24
CHI-11-MS-06 | CHI11: Utilities Available to Owner (Gas Service N/A) | [7 empty] | 26-Dec-24
CHI-11-MS-07 | CHI11: Roofing Complete | [7 empty] | 15-Jan-25
CHI-11-MS-08 | CHI11: Enclosure Complete | [7 empty] | 15-Jan-25
CHI-11-MS-09 | CHI11: Electrical Service Available | [7 empty] | 05-May-25
CHI-11-MS-10 | CHI11: Commissioning Complete | [7 empty] | 19-Nov-25
CHI-11-MS-11 | CHI11: Substantial Completion | [7 empty] | 02-Dec-25
CHI-11-MS-12 | CHI11: Final Completion (SC+40d) | [7 empty] | 22-Jan-26
CHI-11-MS-13 | CHI11: Closeout Complete | [7 empty] | 22-Jan-26
CHI11-03-01-10 | C03/01-DH- Layout Framing | [5 empty] | 17-Jan-25 |  | 17-Jan-25
CHI11-03-01-100 | C03/01-Elec Rm- Overhead R/I - Electrical | [5 empty] | 13-Feb-25 |  | 15-Feb-25
CHI11-03-01-105 | C03/01-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-03-01-110 | C03/01-DH- Paint Secondary Steel | [5 empty] | 15-Feb-25 |  | 17-Feb-25
CHI11-03-01-115 | C03/01-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 15-Feb-25 |  | 15-Feb-25
CHI11-03-01-120 | C03/01-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 15-Feb-25 |  | 17-Feb-25
CHI11-03-01-125 | C03/01-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 15-Feb-25 |  | 18-Feb-25
CHI11-03-01-130 | C03/01-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 17-Feb-25 |  | 18-Feb-25
CHI11-03-01-135 | C03/01-DH- General Cleaning | [5 empty] | 18-Feb-25 |  | 18-Feb-25
CHI11-03-01-140 | C03/01-DH- Install Ceiling Grid | [5 empty] | 18-Feb-25 |  | 21-Feb-25
CHI11-03-01-145 | C03/01-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 19-Feb-25 |  | 25-Feb-25
CHI11-03-01-15 | C03/01-DH- Install Framing | [5 empty] | 20-Jan-25 |  | 24-Jan-25
CHI11-03-01-150 | C03/01-DH- Install Perimeter Cable Trays | [5 empty] | 22-Feb-25 |  | 26-Feb-25
CHI11-03-01-155 | C03/01-DH- Assemble HACs [Qty - 5] | [5 empty] | 22-Feb-25 |  | 27-Feb-25
CHI11-03-01-160 | C03/01-Elec Rm- Finish Dry-Wall | [5 empty] | 22-Feb-25 |  | 04-Mar-25
CHI11-03-01-165 | C03/01-DH- Install Busways on HAC Arms | [5 empty] | 25-Feb-25 |  | 03-Mar-25
CHI11-03-01-170 | C03/01-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 26-Feb-25 |  | 05-Mar-25
CHI11-03-01-175 | C03/01-DH- Install Device Tiles | [5 empty] | 27-Feb-25 |  | 28-Feb-25
CHI11-03-01-180 | C03/01-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 27-Feb-25 |  | 05-Mar-25
CHI11-03-01-185 | C03/01-DH- Set PDUs | [5 empty] | 27-Feb-25 |  | 04-Mar-25
CHI11-03-01-190 | C03/01-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 04-Mar-25 |  | 05-Mar-25
CHI11-03-01-195 | C03/01-Elec Rm- Paint Dry-Wall | [5 empty] | 05-Mar-25 |  | 06-Mar-25
CHI11-03-01-20 | C03/01-DH- In-Wall R/I | [5 empty] | 25-Jan-25 |  | 28-Jan-25
CHI11-03-01-200 | C03/01-DH- Raise HACs | [5 empty] | 06-Mar-25 |  | 10-Mar-25
CHI11-03-01-205 | C03/01-Mech Gallery- Finish Dry-Wall | [5 empty] | 06-Mar-25 |  | 07-Mar-25
CHI11-03-01-210 | C03/01-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 06-Mar-25 |  | 06-Mar-25
CHI11-03-01-215 | C03/01-Elec Rm- General Cleaning | [5 empty] | 07-Mar-25 |  | 07-Mar-25
CHI11-03-01-220 | C03/01-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 07-Mar-25 |  | 11-Mar-25
CHI11-03-01-225 | C03/01-Mech Gallery- Paint Dry-Wall | [5 empty] | 08-Mar-25 |  | 10-Mar-25
CHI11-03-01-230 | C03/01-Elec Rm- Set Electrical Equipments | [5 empty] | 10-Mar-25 |  | 15-Mar-25
CHI11-03-01-235 | C03/01-DH- Detail HACs | [5 empty] | 11-Mar-25 |  | 14-Mar-25
CHI11-03-01-240 | C03/01-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 11-Mar-25 |  | 13-Mar-25
CHI11-03-01-245 | C03/01-Mech Gallery- General Cleaning | [5 empty] | 11-Mar-25 |  | 13-Mar-25
CHI11-03-01-25 | C03/01-Elec Rm- Install Framing | [5 empty] | 25-Jan-25 |  | 30-Jan-25
CHI11-03-01-250 | C03/01-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 12-Mar-25 |  | 13-Mar-25
CHI11-03-01-255 | C03/01-Mech Gallery- Install BAS Equipments | [5 empty] | 12-Mar-25 |  | 24-Mar-25
CHI11-03-01-260 | C03/01-DH- Install Conduits PDU to Cable Trays | [5 empty] | 14-Mar-25 |  | 17-Mar-25
CHI11-03-01-265 | C03/01-Mech Gallery- Set Mechanical Equipments | [5 empty] | 14-Mar-25 |  | 18-Mar-25
CHI11-03-01-270 | C03/01-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | [5 empty] | 17-Mar-25 |  | 29-Mar-25
CHI11-03-01-275 | C03/01-DH- Pull Feeders from PDUs to Busways | [5 empty] | 18-Mar-25 |  | 24-Mar-25
CHI11-03-01-280 | C03/01-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 19-Mar-25 |  | 02-Apr-25
CHI11-03-01-285 | C03/01-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 25-Mar-25 |  | 02-Apr-25
CHI11-03-01-290 | C03/01-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 31-Mar-25 |  | 03-Apr-25
CHI11-03-01-295 | C03/01-DH- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | [5 empty] | 31-Mar-25 |  | 11-Apr-25
CHI11-03-01-30 | C03/01-DH- Overhead R/I - Fire Protection | [5 empty] | 29-Jan-25 |  | 31-Jan-25
CHI11-03-01-300 | C03/01-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 03-Apr-25 |  | 07-Apr-25
CHI11-03-01-305 | C03/01-DH- Terminate PDUs | [5 empty] | 14-Apr-25 |  | 16-Apr-25
CHI11-03-01-310 | C03/01- Punchlist | [5 empty] | 17-Apr-25 |  | 28-Apr-25
CHI11-03-01-315 | C03/01-L2Cx- Yellow Tags | [5 empty] | 05-May-25 |  | 28-May-25
CHI11-03-01-320 | C03/01-L3Cx- Control Power Checks | [5 empty] | 04-Jun-25 |  | 12-Jun-25
CHI11-03-01-325 | C03/01-L3Cx- EPMS Point to Point Checks | [5 empty] | 13-Jun-25 |  | 23-Jun-25
CHI11-03-01-330 | C03/01-L3Cx- FTE Energizations [480v] | [5 empty] | 25-Jun-25 |  | 28-Jun-25
CHI11-03-01-335 | C03/01-L3Cx- Startups | [5 empty] | 30-Jun-25 |  | 15-Jul-25
CHI11-03-01-340 | C03/01-L3Cx- Loadbanking | [5 empty] | 16-Jul-25 |  | 19-Jul-25
CHI11-03-01-35 | C03/01-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 29-Jan-25 |  | 31-Jan-25
CHI11-03-01-40 | C03/01-Elec Rm- In-Wall R/I | [5 empty] | 31-Jan-25 |  | 10-Feb-25
CHI11-03-01-45 | C03/01-DH- Overhead R/I - Fire Alarm | [5 empty] | 01-Feb-25 |  | 04-Feb-25
CHI11-03-01-50 | C03/01-DH- Overhead R/I - Electrical | [5 empty] | 01-Feb-25 |  | 05-Feb-25
CHI11-03-01-55 | C03/01-DH- Finish Dry-Wall | [5 empty] | 01-Feb-25 |  | 04-Feb-25
CHI11-03-01-60 | C03/01-DH- Overhead R/I - Mechanical | [5 empty] | 04-Feb-25 |  | 05-Feb-25
CHI11-03-01-65 | C03/01-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 06-Feb-25 |  | 07-Feb-25
CHI11-03-01-70 | C03/01-DH- Paint Dry-Wall | [5 empty] | 05-Feb-25 |  | 07-Feb-25
CHI11-03-01-75 | C03/01-DH- Install Screen Mesh + Caulking | [5 empty] | 10-Feb-25 |  | 12-Feb-25
CHI11-03-01-80 | C03/01-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 11-Feb-25 |  | 12-Feb-25
CHI11-03-01-85 | C03/01-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 11-Feb-25 |  | 21-Feb-25
CHI11-03-01-90 | C03/01-DH- Install Secondary Steel | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-03-01-95 | C03/01-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-03-02-10 | C03/02-DH- Layout Framing | [5 empty] | 29-Jan-25 |  | 29-Jan-25
CHI11-03-02-100 | C03/02-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 13-Feb-25 |  | 13-Feb-25
CHI11-03-02-105 | C03/02-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-03-02-110 | C03/02-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 13-Feb-25 |  | 15-Feb-25
CHI11-03-02-115 | C03/02-DH- Paint Dry-Wall | [5 empty] | 14-Feb-25 |  | 17-Feb-25
CHI11-03-02-120 | C03/02-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 14-Feb-25 |  | 15-Feb-25
CHI11-03-02-125 | C03/02-Elec Rm- Paint Dry-Wall | [5 empty] | 15-Feb-25 |  | 17-Feb-25
CHI11-03-02-130 | C03/02-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 17-Feb-25 |  | 22-Feb-25
CHI11-03-02-135 | C03/02-DH- Install Screen Mesh + Caulking | [5 empty] | 18-Feb-25 |  | 20-Feb-25
CHI11-03-02-140 | C03/02-Elec Rm- General Cleaning | [5 empty] | 18-Feb-25 |  | 18-Feb-25
CHI11-03-02-145 | C03/02-DH- Install Secondary Steel | [5 empty] | 21-Feb-25 |  | 22-Feb-25
CHI11-03-02-15 | C03/02-DH- Install Framing | [5 empty] | 30-Jan-25 |  | 01-Feb-25
CHI11-03-02-150 | C03/02-DH- Paint Secondary Steel | [5 empty] | 24-Feb-25 |  | 25-Feb-25
CHI11-03-02-155 | C03/02-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 24-Feb-25 |  | 03-Mar-25
CHI11-03-02-160 | C03/02-DH- General Cleaning | [5 empty] | 26-Feb-25 |  | 26-Feb-25
CHI11-03-02-165 | C03/02-DH- Install Ceiling Grid | [5 empty] | 26-Feb-25 |  | 03-Mar-25
CHI11-03-02-170 | C03/02-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 28-Feb-25 |  | 03-Mar-25
CHI11-03-02-175 | C03/02-DH- Install Perimeter Cable Trays | [5 empty] | 04-Mar-25 |  | 07-Mar-25
CHI11-03-02-180 | C03/02-DH- Assemble HACs [Qty - 5] | [5 empty] | 04-Mar-25 |  | 08-Mar-25
CHI11-03-02-185 | C03/02-Mech Gallery- Finish Dry-Wall | [5 empty] | 04-Mar-25 |  | 05-Mar-25
CHI11-03-02-190 | C03/02-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 04-Mar-25 |  | 04-Mar-25
CHI11-03-02-195 | C03/02-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 05-Mar-25 |  | 08-Mar-25
CHI11-03-02-20 | C03/02-DH- In-Wall R/I | [5 empty] | 03-Feb-25 |  | 05-Feb-25
CHI11-03-02-200 | C03/02-DH- Install Busways on HAC Arms | [5 empty] | 06-Mar-25 |  | 11-Mar-25
CHI11-03-02-205 | C03/02-Mech Gallery- Paint Dry-Wall | [5 empty] | 06-Mar-25 |  | 07-Mar-25
CHI11-03-02-210 | C03/02-DH- Install Device Tiles | [5 empty] | 08-Mar-25 |  | 10-Mar-25
CHI11-03-02-215 | C03/02-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 08-Mar-25 |  | 13-Mar-25
CHI11-03-02-220 | C03/02-DH- Set PDUs | [5 empty] | 08-Mar-25 |  | 12-Mar-25
CHI11-03-02-225 | C03/02-Mech Gallery- General Cleaning | [5 empty] | 08-Mar-25 |  | 11-Mar-25
CHI11-03-02-230 | C03/02-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 10-Mar-25 |  | 11-Mar-25
CHI11-03-02-235 | C03/02-Mech Gallery- Install BAS Equipments | [5 empty] | 10-Mar-25 |  | 20-Mar-25
CHI11-03-02-240 | C03/02-Mech Gallery- Set Mechanical Equipments | [5 empty] | 12-Mar-25 |  | 15-Mar-25
CHI11-03-02-245 | C03/02-DH- Raise HACs | [5 empty] | 14-Mar-25 |  | 18-Mar-25
CHI11-03-02-25 | C03/02-Elec Rm- Install Framing | [5 empty] | 03-Feb-25 |  | 04-Feb-25
CHI11-03-02-250 | C03/02-Elec Rm- Set Electrical Equipments | [5 empty] | 17-Mar-25 |  | 20-Mar-25
CHI11-03-02-255 | C03/02-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 17-Mar-25 |  | 31-Mar-25
CHI11-03-02-260 | C03/02-DH- Detail HACs | [5 empty] | 19-Mar-25 |  | 24-Mar-25
CHI11-03-02-265 | C03/02-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 19-Mar-25 |  | 21-Mar-25
CHI11-03-02-270 | C03/02-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 21-Mar-25 |  | 31-Mar-25
CHI11-03-02-275 | C03/02-DH- Install Conduits PDU to Cable Trays | [5 empty] | 24-Mar-25 |  | 26-Mar-25
CHI11-03-02-280 | C03/C02- Punchlist | [5 empty] | 13-May-25 |  | 23-May-25
CHI11-03-02-285 | C03/02-DH- Pull Feeders from PDUs to Busways | [5 empty] | 27-Mar-25 |  | 01-Apr-25
CHI11-03-02-290 | C03/02-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 01-Apr-25 |  | 04-Apr-25
CHI11-03-02-295 | C03/02-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | [5 empty] | 14-Apr-25 |  | 25-Apr-25
CHI11-03-02-30 | C03/02-Elec Rm- In-Wall R/I | [5 empty] | 05-Feb-25 |  | 06-Feb-25
CHI11-03-02-300 | C03/02-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 26-Apr-25 |  | 30-Apr-25
CHI11-03-02-305 | C03/02-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | [5 empty] | 26-Apr-25 |  | 08-May-25
CHI11-03-02-310 | C03/02-DH- Terminate PDUs | [5 empty] | 09-May-25 |  | 12-May-25
CHI11-03-02-315 | C03/02-L2Cx- Yellow Tags | [5 empty] | 15-May-25 |  | 07-Jun-25
CHI11-03-02-320 | C03/02-L3Cx- Control Power Checks | [5 empty] | 09-Jun-25 |  | 18-Jun-25
CHI11-03-02-325 | C03/02-L3Cx- EPMS Point to Point Checks | [5 empty] | 19-Jun-25 |  | 27-Jun-25
CHI11-03-02-330 | C03/02-L3Cx- FTE Energizations [480v] | [5 empty] | 28-Jun-25 |  | 02-Jul-25
CHI11-03-02-335 | C03/02-L3Cx- Startups | [5 empty] | 03-Jul-25 |  | 18-Jul-25
CHI11-03-02-340 | C03/02-L3Cx- Loadbanking | [5 empty] | 21-Jul-25 |  | 24-Jul-25
CHI11-03-02-35 | C03/02-DH- Overhead R/I - Fire Protection | [5 empty] | 06-Feb-25 |  | 10-Feb-25
CHI11-03-02-40 | C03/02-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 06-Feb-25 |  | 10-Feb-25
CHI11-03-02-45 | C03/02-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 07-Feb-25 |  | 10-Feb-25
CHI11-03-02-50 | C03/02-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 07-Feb-25 |  | 12-Feb-25
CHI11-03-02-55 | C03/02-DH- Overhead R/I - Fire Alarm | [5 empty] | 11-Feb-25 |  | 13-Feb-25
CHI11-03-02-60 | C03/02-DH- Overhead R/I - Electrical | [5 empty] | 11-Feb-25 |  | 14-Feb-25
CHI11-03-02-65 | C03/02-DH- Finish Dry-Wall | [5 empty] | 11-Feb-25 |  | 13-Feb-25
CHI11-03-02-70 | C03/02-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 11-Feb-25 |  | 12-Feb-25
CHI11-03-02-75 | C03/02-Elec Rm- Overhead R/I - Electrical | [5 empty] | 11-Feb-25 |  | 13-Feb-25
CHI11-03-02-80 | C03/02-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 11-Feb-25 |  | 12-Feb-25
CHI11-03-02-85 | C03/02-DH- Overhead R/I - Mechanical | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-03-02-90 | C03/02-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-03-02-95 | C03/02-Elec Rm- Finish Dry-Wall | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-03-03-10 | C03/03-DH- Layout Framing | [5 empty] | 21-Feb-25 |  | 21-Feb-25
CHI11-03-03-100 | C03/03-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 08-Mar-25 |  | 08-Mar-25
CHI11-03-03-105 | C03/03-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 08-Mar-25 |  | 10-Mar-25
CHI11-03-03-110 | C03/03-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 08-Mar-25 |  | 11-Mar-25
CHI11-03-03-115 | C03/03-DH- Paint Dry-Wall | [5 empty] | 10-Mar-25 |  | 12-Mar-25
CHI11-03-03-120 | C03/03-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 10-Mar-25 |  | 11-Mar-25
CHI11-03-03-125 | C03/03-Elec Rm- Paint Dry-Wall | [5 empty] | 11-Mar-25 |  | 12-Mar-25
CHI11-03-03-130 | C03/03-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 12-Mar-25 |  | 18-Mar-25
CHI11-03-03-135 | C03/03-DH- Install Screen Mesh + Caulking | [5 empty] | 13-Mar-25 |  | 15-Mar-25
CHI11-03-03-140 | C03/03-Elec Rm- General Cleaning | [5 empty] | 13-Mar-25 |  | 13-Mar-25
CHI11-03-03-145 | C03/03-Elec Rm- Set Electrical Equipments | [5 empty] | 14-Mar-25 |  | 18-Mar-25
CHI11-03-03-15 | C03/03-DH- Install Framing | [5 empty] | 22-Feb-25 |  | 25-Feb-25
CHI11-03-03-150 | C03/03-DH- Install Secondary Steel | [5 empty] | 17-Mar-25 |  | 18-Mar-25
CHI11-03-03-155 | C03/03-DH- Paint Secondary Steel | [5 empty] | 19-Mar-25 |  | 20-Mar-25
CHI11-03-03-160 | C03/03-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 19-Mar-25 |  | 26-Mar-25
CHI11-03-03-165 | C03/03-DH- General Cleaning | [5 empty] | 21-Mar-25 |  | 21-Mar-25
CHI11-03-03-170 | C03/03-DH- Install Ceiling Grid | [5 empty] | 21-Mar-25 |  | 26-Mar-25
CHI11-03-03-175 | C03/03-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 25-Mar-25 |  | 26-Mar-25
CHI11-03-03-180 | C03/03-DH- Install Perimeter Cable Trays | [5 empty] | 27-Mar-25 |  | 31-Mar-25
CHI11-03-03-185 | C03/03-DH- Assemble HACs [Qty - 5] | [5 empty] | 27-Mar-25 |  | 01-Apr-25
CHI11-03-03-190 | C03/03-Mech Gallery- Finish Dry-Wall | [5 empty] | 27-Mar-25 |  | 28-Mar-25
CHI11-03-03-195 | C03/03-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 27-Mar-25 |  | 27-Mar-25
CHI11-03-03-20 | C03/03-DH- In-Wall R/I | [5 empty] | 26-Feb-25 |  | 28-Feb-25
CHI11-03-03-200 | C03/03-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 28-Mar-25 |  | 01-Apr-25
CHI11-03-03-205 | C03/03-DH- Install Busways on HAC Arms | [5 empty] | 29-Mar-25 |  | 03-Apr-25
CHI11-03-03-210 | C03/03-Mech Gallery- Paint Dry-Wall | [5 empty] | 29-Mar-25 |  | 31-Mar-25
CHI11-03-03-215 | C03/03-DH- Install Device Tiles | [5 empty] | 01-Apr-25 |  | 02-Apr-25
CHI11-03-03-220 | C03/03-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 01-Apr-25 |  | 05-Apr-25
CHI11-03-03-225 | C03/03-DH- Set PDUs | [5 empty] | 01-Apr-25 |  | 04-Apr-25
CHI11-03-03-230 | C03/03-Mech Gallery- General Cleaning | [5 empty] | 01-Apr-25 |  | 03-Apr-25
CHI11-03-03-235 | C03/03-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 02-Apr-25 |  | 03-Apr-25
CHI11-03-03-240 | C03/03-Mech Gallery- Install BAS Equipments | [5 empty] | 02-Apr-25 |  | 14-Apr-25
CHI11-03-03-245 | C03/03-Mech Gallery- Set Mechanical Equipments | [5 empty] | 04-Apr-25 |  | 08-Apr-25
CHI11-03-03-25 | C03/03-Elec Rm- Install Framing | [5 empty] | 26-Feb-25 |  | 27-Feb-25
CHI11-03-03-250 | C03/03-DH- Raise HACs | [5 empty] | 07-Apr-25 |  | 10-Apr-25
CHI11-03-03-255 | C03/03-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 09-Apr-25 |  | 23-Apr-25
CHI11-03-03-260 | C03/03-DH- Detail HACs | [5 empty] | 11-Apr-25 |  | 16-Apr-25
CHI11-03-03-265 | C03/03-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 11-Apr-25 |  | 15-Apr-25
CHI11-03-03-270 | C03/03-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 15-Apr-25 |  | 23-Apr-25
CHI11-03-03-275 | C03/03-DH- Install Conduits PDU to Cable Trays | [5 empty] | 16-Apr-25 |  | 18-Apr-25
CHI11-03-03-280 | C03/03- Punchlist | [5 empty] | 09-Jun-25 |  | 20-Jun-25
CHI11-03-03-285 | C03/03-DH- Pull Feeders from PDUs to Busways | [5 empty] | 19-Apr-25 |  | 24-Apr-25
CHI11-03-03-290 | C03/03-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 24-Apr-25 |  | 28-Apr-25
CHI11-03-03-295 | C03/03-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | [5 empty] | 10-May-25 |  | 22-May-25
CHI11-03-03-30 | C03/03-Elec Rm- In-Wall R/I | [5 empty] | 28-Feb-25 |  | 03-Mar-25
CHI11-03-03-300 | C03/03-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 23-May-25 |  | 28-May-25
CHI11-03-03-305 | C03/03-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | [5 empty] | 23-May-25 |  | 04-Jun-25
CHI11-03-03-310 | C03/03-DH- Terminate PDUs | [5 empty] | 05-Jun-25 |  | 07-Jun-25
CHI11-03-03-315 | C03/03-L2Cx- Yellow Tags | [5 empty] | 09-Jun-25 |  | 02-Jul-25
CHI11-03-03-320 | C03/03-L3Cx- Control Power Checks | [5 empty] | 24-Jun-25 |  | 07-Jul-25
CHI11-03-03-325 | C03/03-L3Cx- EPMS Point to Point Checks | [5 empty] | 08-Jul-25 |  | 18-Jul-25
CHI11-03-03-330 | C03/03-L3Cx- FTE Energizations [480v] | [5 empty] | 19-Jul-25 |  | 24-Jul-25
CHI11-03-03-335 | C03/03-L3Cx- Startups | [5 empty] | 25-Jul-25 |  | 08-Aug-25
CHI11-03-03-340 | C03/03-L3Cx- Loadbanking | [5 empty] | 09-Aug-25 |  | 14-Aug-25
CHI11-03-03-35 | C03/03-DH- Overhead R/I - Fire Protection | [5 empty] | 03-Mar-25 |  | 05-Mar-25
CHI11-03-03-40 | C03/03-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 03-Mar-25 |  | 05-Mar-25
CHI11-03-03-45 | C03/03-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 04-Mar-25 |  | 05-Mar-25
CHI11-03-03-50 | C03/03-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 04-Mar-25 |  | 07-Mar-25
CHI11-03-03-55 | C03/03-DH- Overhead R/I - Fire Alarm | [5 empty] | 06-Mar-25 |  | 08-Mar-25
CHI11-03-03-60 | C03/03-DH- Overhead R/I - Electrical | [5 empty] | 06-Mar-25 |  | 10-Mar-25
CHI11-03-03-65 | C03/03-DH- Finish Dry-Wall | [5 empty] | 06-Mar-25 |  | 08-Mar-25
CHI11-03-03-70 | C03/03-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 06-Mar-25 |  | 07-Mar-25
CHI11-03-03-75 | C03/03-Elec Rm- Overhead R/I - Electrical | [5 empty] | 06-Mar-25 |  | 08-Mar-25
CHI11-03-03-80 | C03/03-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 06-Mar-25 |  | 07-Mar-25
CHI11-03-03-85 | C03/03-DH- Overhead R/I - Mechanical | [5 empty] | 08-Mar-25 |  | 10-Mar-25
CHI11-03-03-90 | C03/03-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 08-Mar-25 |  | 10-Mar-25
CHI11-03-03-95 | C03/03-Elec Rm- Finish Dry-Wall | [5 empty] | 08-Mar-25 |  | 10-Mar-25
CHI11-03-04-10 | C03/04-DH- Layout Framing | [5 empty] | 10-Feb-25 |  | 10-Feb-25
CHI11-03-04-100 | C03/04-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 24-Feb-25 |  | 24-Feb-25
CHI11-03-04-105 | C03/04-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 24-Feb-25 |  | 25-Feb-25
CHI11-03-04-110 | C03/04-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 24-Feb-25 |  | 26-Feb-25
CHI11-03-04-115 | C03/04-DH- Paint Dry-Wall | [5 empty] | 25-Feb-25 |  | 27-Feb-25
CHI11-03-04-120 | C03/04-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 25-Feb-25 |  | 26-Feb-25
CHI11-03-04-125 | C03/04-Elec Rm- Paint Dry-Wall | [5 empty] | 26-Feb-25 |  | 27-Feb-25
CHI11-03-04-130 | C03/04-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 27-Feb-25 |  | 06-Mar-25
CHI11-03-04-135 | C03/04-DH- Install Screen Mesh + Caulking | [5 empty] | 28-Feb-25 |  | 04-Mar-25
CHI11-03-04-140 | C03/04-Elec Rm- General Cleaning | [5 empty] | 28-Feb-25 |  | 28-Feb-25
CHI11-03-04-145 | C03/04-Elec Rm- Set Electrical Equipments | [5 empty] | 03-Mar-25 |  | 06-Mar-25
CHI11-03-04-15 | C03/04-DH- Install Framing | [5 empty] | 11-Feb-25 |  | 13-Feb-25
CHI11-03-04-150 | C03/04-DH- Install Secondary Steel | [5 empty] | 05-Mar-25 |  | 06-Mar-25
CHI11-03-04-155 | C03/04-DH- Paint Secondary Steel | [5 empty] | 07-Mar-25 |  | 08-Mar-25
CHI11-03-04-160 | C03/04-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | [5 empty] | 07-Mar-25 |  | 19-Mar-25
CHI11-03-04-165 | C03/04-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 07-Mar-25 |  | 13-Mar-25
CHI11-03-04-170 | C03/04-DH- General Cleaning | [5 empty] | 10-Mar-25 |  | 10-Mar-25
CHI11-03-04-175 | C03/04-DH- Install Ceiling Grid | [5 empty] | 10-Mar-25 |  | 13-Mar-25
CHI11-03-04-180 | C03/04-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 12-Mar-25 |  | 13-Mar-25
CHI11-03-04-185 | C03/04-DH- Install Perimeter Cable Trays | [5 empty] | 14-Mar-25 |  | 18-Mar-25
CHI11-03-04-190 | C03/04-DH- Assemble HACs [Qty - 5] | [5 empty] | 14-Mar-25 |  | 19-Mar-25
CHI11-03-04-195 | C03/04-Mech Gallery- Finish Dry-Wall | [5 empty] | 14-Mar-25 |  | 15-Mar-25
CHI11-03-04-20 | C03/04-DH- In-Wall R/I | [5 empty] | 14-Feb-25 |  | 17-Feb-25
CHI11-03-04-200 | C03/04-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 14-Mar-25 |  | 14-Mar-25
CHI11-03-04-205 | C03/04-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 15-Mar-25 |  | 19-Mar-25
CHI11-03-04-210 | C03/04-DH- Install Busways on HAC Arms | [5 empty] | 17-Mar-25 |  | 21-Mar-25
CHI11-03-04-215 | C03/04-Mech Gallery- Paint Dry-Wall | [5 empty] | 17-Mar-25 |  | 18-Mar-25
CHI11-03-04-220 | C03/04-DH- Install Device Tiles | [5 empty] | 19-Mar-25 |  | 20-Mar-25
CHI11-03-04-225 | C03/04-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 19-Mar-25 |  | 25-Mar-25
CHI11-03-04-230 | C03/04-DH- Set PDUs | [5 empty] | 19-Mar-25 |  | 24-Mar-25
CHI11-03-04-235 | C03/04-Mech Gallery- General Cleaning | [5 empty] | 19-Mar-25 |  | 21-Mar-25
CHI11-03-04-240 | C03/04-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 20-Mar-25 |  | 25-Mar-25
CHI11-03-04-245 | C03/04-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 20-Mar-25 |  | 21-Mar-25
CHI11-03-04-25 | C03/04-Elec Rm- Install Framing | [5 empty] | 14-Feb-25 |  | 15-Feb-25
CHI11-03-04-250 | C03/04-Mech Gallery- Install BAS Equipments | [5 empty] | 20-Mar-25 |  | 01-Apr-25
CHI11-03-04-255 | C03/04-Mech Gallery- Set Mechanical Equipments | [5 empty] | 24-Mar-25 |  | 27-Mar-25
CHI11-03-04-260 | C03/04-DH- Raise HACs | [5 empty] | 26-Mar-25 |  | 29-Mar-25
CHI11-03-04-265 | C03/04-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 28-Mar-25 |  | 10-Apr-25
CHI11-03-04-270 | C03/04-DH- Detail HACs | [5 empty] | 31-Mar-25 |  | 03-Apr-25
CHI11-03-04-275 | C03/04-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 31-Mar-25 |  | 02-Apr-25
CHI11-03-04-280 | C03/04-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 02-Apr-25 |  | 10-Apr-25
CHI11-03-04-285 | C03/04-DH- Install Conduits PDU to Cable Trays | [5 empty] | 03-Apr-25 |  | 05-Apr-25
CHI11-03-04-290 | C03/04- Punchlist | [5 empty] | 10-May-25 |  | 21-May-25
CHI11-03-04-295 | C03/04-DH- Pull Feeders from PDUs to Busways | [5 empty] | 07-Apr-25 |  | 11-Apr-25
CHI11-03-04-30 | C03/04-Elec Rm- In-Wall R/I | [5 empty] | 17-Feb-25 |  | 18-Feb-25
CHI11-03-04-300 | C03/04-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 11-Apr-25 |  | 16-Apr-25
CHI11-03-04-305 | C03/04-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | [5 empty] | 26-Apr-25 |  | 09-May-25
CHI11-03-04-310 | C03/04-DH- Terminate PDUs | [5 empty] | 10-May-25 |  | 13-May-25
CHI11-03-04-315 | C03/04-L2Cx- Yellow Tags | [5 empty] | 27-May-25 |  | 18-Jun-25
CHI11-03-04-320 | C03/04-L3Cx- Control Power Checks | [5 empty] | 13-Jun-25 |  | 23-Jun-25
CHI11-03-04-325 | C03/04-L3Cx- EPMS Point to Point Checks | [5 empty] | 24-Jun-25 |  | 02-Jul-25
CHI11-03-04-330 | C03/04-L3Cx- FTE Energizations [480v] | [5 empty] | 03-Jul-25 |  | 09-Jul-25
CHI11-03-04-335 | C03/04-L3Cx- Startups | [5 empty] | 10-Jul-25 |  | 23-Jul-25
CHI11-03-04-340 | C03/04-L3Cx- Loadbanking | [5 empty] | 25-Jul-25 |  | 30-Jul-25
CHI11-03-04-35 | C03/04-DH- Overhead R/I - Fire Protection | [5 empty] | 18-Feb-25 |  | 20-Feb-25
CHI11-03-04-40 | C03/04-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 18-Feb-25 |  | 20-Feb-25
CHI11-03-04-45 | C03/04-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 19-Feb-25 |  | 20-Feb-25
CHI11-03-04-50 | C03/04-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 19-Feb-25 |  | 22-Feb-25
CHI11-03-04-55 | C03/04-DH- Overhead R/I - Fire Alarm | [5 empty] | 21-Feb-25 |  | 24-Feb-25
CHI11-03-04-60 | C03/04-DH- Overhead R/I - Electrical | [5 empty] | 21-Feb-25 |  | 25-Feb-25
CHI11-03-04-65 | C03/04-DH- Finish Dry-Wall | [5 empty] | 21-Feb-25 |  | 24-Feb-25
CHI11-03-04-70 | C03/04-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 21-Feb-25 |  | 22-Feb-25
CHI11-03-04-75 | C03/04-Elec Rm- Overhead R/I - Electrical | [5 empty] | 21-Feb-25 |  | 24-Feb-25
CHI11-03-04-80 | C03/04-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 21-Feb-25 |  | 22-Feb-25
CHI11-03-04-85 | C03/04-DH- Overhead R/I - Mechanical | [5 empty] | 24-Feb-25 |  | 25-Feb-25
CHI11-03-04-90 | C03/04-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 24-Feb-25 |  | 25-Feb-25
CHI11-03-04-95 | C03/04-Elec Rm- Finish Dry-Wall | [5 empty] | 24-Feb-25 |  | 25-Feb-25
CHI11-03-C&S-10 | Admin/C03- Install Primary Steel | [5 empty] | 14-Oct-2024 |  | 07-Nov-2024
CHI11-03-C&S-15 | Admin/C03- Install Roof Panels | [5 empty] | 30-Nov-24 |  | 14-Dec-24
CHI11-03-C&S-20 | Admin/C03- UG MEP Work AMS/Gibson | [5 empty] | 13-Nov-2024 |  | 14-Dec-24
CHI11-03-C&S-25 | Admin/C03- Install Exterior Wall Panels | [5 empty] | 18-Nov-2024 |  | 29-Nov-24
CHI11-03-C&S-30 | Admin/C03- Install Louvers & Dampers | [5 empty] | 16-Dec-24 |  | 06-Jan-25
CHI11-03-C&S-35 | Admin/C03- Prep / Place SOG | [5 empty] | 16-Dec-24 |  | 27-Dec-24
CHI11-03-C&S-40 | Admin/C03- Install Misc. Metals (Trims, Gutters, Catwalks) | [5 empty] | 30-Dec-24 |  | 17-Jan-25
CHI11-03-C&S-45 | Admin/C03- Weather Days | [5 empty] | 30-Dec-24 |  | 16-Jan-25
CHI11-03-L3-10 | C03-L3Cx- Install Metering Cabinet [Prior to Energization] | [5 empty] | 19-Jun-25 |  | 24-Jun-25
CHI11-03-L4-10 | C03-L4Cx- Testing <MSFT Duration> | [5 empty] | 15-Aug-25 |  | 15-Sep-25
CHI11-03-L5-10 | C03-L5Cx- Testing <MSFT Duration> | [5 empty] | 16-Sep-25 |  | 18-Sep-25
CHI11-03-YARD-10 | C03/Yard- Build Equipment Pads for XFMs | [5 empty] | 17-Jan-25 |  | 28-Jan-25
CHI11-03-YARD-15 | C03/Yard- Build Equipment Pads for UPMs | [5 empty] | 29-Jan-25 |  | 07-Feb-25
CHI11-03-YARD-20 | C03/Yard- Build Equipment Pads for UMSs | [5 empty] | 10-Feb-25 |  | 19-Feb-25
CHI11-03-YARD-25 | C03/Yard- Build Equipment Pads for Generators | [5 empty] | 20-Feb-25 |  | 03-Mar-25
CHI11-03-YARD-30 | C03/Yard- Install XFMs | [5 empty] | 04-Mar-25 |  | 15-Mar-25
CHI11-03-YARD-35 | C03/Yard- Install UPMs | [5 empty] | 04-Mar-25 |  | 15-Mar-25
CHI11-03-YARD-40 | C03/Yard- Install UMSs | [5 empty] | 04-Mar-25 |  | 15-Mar-25
CHI11-03-YARD-45 | C03/Yard- Install Generators | [5 empty] | 04-Mar-25 |  | 15-Mar-25
CHI11-03-YARD-50 | C03/Yard- MV Cable Pulling & Terminating to Cell 1 | [5 empty] | 25-Apr-25 |  | 05-May-25
CHI11-03-YARD-55 | C03/Yard- MV Cable Pulling & Terminating to Cell 2 | [5 empty] | 06-May-25 |  | 14-May-25
CHI11-03-YARD-60 | C03/Yard- MV Cable Pulling & Terminating to Cell 4 | [5 empty] | 15-May-25 |  | 23-May-25
CHI11-03-YARD-65 | C03/Yard- MV Cable Pulling & Terminating to Cell 3 | [5 empty] | 27-May-25 |  | 03-Jun-25
CHI11-04-01-10 | C04/01-DH- Layout Framing | [5 empty] | 24-Feb-25 |  | 24-Feb-25
CHI11-04-01-100 | C04/01-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 11-Mar-25 |  | 11-Mar-25
CHI11-04-01-105 | C04/01-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 11-Mar-25 |  | 12-Mar-25
CHI11-04-01-110 | C04/01-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 11-Mar-25 |  | 13-Mar-25
CHI11-04-01-115 | C04/01-DH- Paint Dry-Wall | [5 empty] | 12-Mar-25 |  | 14-Mar-25
CHI11-04-01-120 | C04/01-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 12-Mar-25 |  | 13-Mar-25
CHI11-04-01-125 | C04/01-Elec Rm- Paint Dry-Wall | [5 empty] | 13-Mar-25 |  | 14-Mar-25
CHI11-04-01-130 | C04/01-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 14-Mar-25 |  | 20-Mar-25
CHI11-04-01-135 | C04/01-DH- Install Screen Mesh + Caulking | [5 empty] | 15-Mar-25 |  | 18-Mar-25
CHI11-04-01-140 | C04/01-Elec Rm- General Cleaning | [5 empty] | 15-Mar-25 |  | 15-Mar-25
CHI11-04-01-145 | C04/01-DH- Install Secondary Steel | [5 empty] | 19-Mar-25 |  | 20-Mar-25
CHI11-04-01-15 | C04/01-DH- IInstall Framing | [5 empty] | 25-Feb-25 |  | 27-Feb-25
CHI11-04-01-150 | C04/01-DH- Paint Secondary Steel | [5 empty] | 21-Mar-25 |  | 24-Mar-25
CHI11-04-01-155 | C04/01-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 21-Mar-25 |  | 28-Mar-25
CHI11-04-01-160 | C04/01-DH- General Cleaning | [5 empty] | 25-Mar-25 |  | 25-Mar-25
CHI11-04-01-165 | C04/01-DH- Install Ceiling Grid | [5 empty] | 25-Mar-25 |  | 28-Mar-25
CHI11-04-01-170 | C04/01-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 27-Mar-25 |  | 28-Mar-25
CHI11-04-01-175 | C04/01-DH- Install Perimeter Cable Trays | [5 empty] | 29-Mar-25 |  | 02-Apr-25
CHI11-04-01-180 | C04/01-DH- Assemble HACs [Qty - 5] | [5 empty] | 29-Mar-25 |  | 03-Apr-25
CHI11-04-01-185 | C04/01-Mech Gallery- Finish Dry-Wall | [5 empty] | 29-Mar-25 |  | 31-Mar-25
CHI11-04-01-190 | C04/01-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 29-Mar-25 |  | 29-Mar-25
CHI11-04-01-195 | C04/01-Elec Rm- Set Electrical Equipments | [5 empty] | 31-Mar-25 |  | 03-Apr-25
CHI11-04-01-20 | C04/01-DH- In-Wall R/I | [5 empty] | 28-Feb-25 |  | 04-Mar-25
CHI11-04-01-200 | C04/01-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 31-Mar-25 |  | 03-Apr-25
CHI11-04-01-205 | C04/01-DH- Install Busways on HAC Arms | [5 empty] | 01-Apr-25 |  | 05-Apr-25
CHI11-04-01-210 | C04/01-Mech Gallery- Paint Dry-Wall | [5 empty] | 01-Apr-25 |  | 02-Apr-25
CHI11-04-01-215 | C04/01-DH- Install Device Tiles | [5 empty] | 03-Apr-25 |  | 04-Apr-25
CHI11-04-01-220 | C04/01-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 03-Apr-25 |  | 08-Apr-25
CHI11-04-01-225 | C04/01-DH- Set PDUs | [5 empty] | 03-Apr-25 |  | 07-Apr-25
CHI11-04-01-230 | C04/01-Mech Gallery- General Cleaning | [5 empty] | 03-Apr-25 |  | 05-Apr-25
CHI11-04-01-235 | C04/01-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | [5 empty] | 04-Apr-25 |  | 17-Apr-25
CHI11-04-01-240 | C04/01-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 04-Apr-25 |  | 05-Apr-25
CHI11-04-01-245 | C04/01-Mech Gallery- Install BAS Equipments | [5 empty] | 04-Apr-25 |  | 16-Apr-25
CHI11-04-01-25 | C04/01-Elec Rm- Install Framing | [5 empty] | 28-Feb-25 |  | 03-Mar-25
CHI11-04-01-250 | C04/01-Mech Gallery- Set Mechanical Equipments | [5 empty] | 07-Apr-25 |  | 10-Apr-25
CHI11-04-01-255 | C04/01-DH- Raise HACs | [5 empty] | 09-Apr-25 |  | 14-Apr-25
CHI11-04-01-260 | C04/01-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 11-Apr-25 |  | 25-Apr-25
CHI11-04-01-265 | C04/01-DH- Detail HACs | [5 empty] | 15-Apr-25 |  | 18-Apr-25
CHI11-04-01-270 | C04/01-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 15-Apr-25 |  | 17-Apr-25
CHI11-04-01-275 | C04/01-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 17-Apr-25 |  | 25-Apr-25
CHI11-04-01-280 | C04/01-DH- Install Conduits PDU to Cable Trays | [5 empty] | 18-Apr-25 |  | 21-Apr-25
CHI11-04-01-285 | C04/01-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 18-Apr-25 |  | 22-Apr-25
CHI11-04-01-290 | C04/01-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | [5 empty] | 18-Apr-25 |  | 30-Apr-25
CHI11-04-01-295 | C04/01- Punchlist | [5 empty] | 06-May-25 |  | 16-May-25
CHI11-04-01-30 | C04/01-Elec Rm- In-Wall R/I | [5 empty] | 04-Mar-25 |  | 05-Mar-25
CHI11-04-01-300 | C04/01-DH- Pull Feeders from PDUs to Busways | [5 empty] | 22-Apr-25 |  | 26-Apr-25
CHI11-04-01-305 | C04/01-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 26-Apr-25 |  | 30-Apr-25
CHI11-04-01-310 | C04/01-DH- Terminate PDUs | [5 empty] | 01-May-25 |  | 05-May-25
CHI11-04-01-315 | C04/01-L2Cx- Yellow Tags | [5 empty] | 06-May-25 |  | 29-May-25
CHI11-04-01-320 | C04/01-L3Cx- Control Power Checks | [5 empty] | 20-Jun-25 |  | 28-Jun-25
CHI11-04-01-325 | C04/01-L3Cx- EPMS Point to Point Checks | [5 empty] | 30-Jun-25 |  | 10-Jul-25
CHI11-04-01-330 | C04/01-L3Cx- FTE Energizations [480v] | [5 empty] | 11-Jul-25 |  | 15-Jul-25
CHI11-04-01-335 | C04/01-L3Cx- Startups | [5 empty] | 16-Jul-25 |  | 30-Jul-25
CHI11-04-01-340 | C04/01-L3Cx- Loadbanking | [5 empty] | 31-Jul-25 |  | 04-Aug-25
CHI11-04-01-35 | C04/01-DH- Overhead R/I - Fire Protection | [5 empty] | 05-Mar-25 |  | 07-Mar-25
CHI11-04-01-40 | C04/01-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 05-Mar-25 |  | 07-Mar-25
CHI11-04-01-45 | C04/01-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 06-Mar-25 |  | 07-Mar-25
CHI11-04-01-50 | C04/01-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 06-Mar-25 |  | 10-Mar-25
CHI11-04-01-55 | C04/01-DH- Overhead R/I - Fire Alarm | [5 empty] | 08-Mar-25 |  | 11-Mar-25
CHI11-04-01-60 | C04/01-DH- Overhead R/I - Electrical | [5 empty] | 08-Mar-25 |  | 12-Mar-25
CHI11-04-01-65 | C04/01-DH- Finish Dry-Wall | [5 empty] | 08-Mar-25 |  | 11-Mar-25
CHI11-04-01-70 | C04/01-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 08-Mar-25 |  | 10-Mar-25
CHI11-04-01-75 | C04/01-Elec Rm- Overhead R/I - Electrical | [5 empty] | 08-Mar-25 |  | 11-Mar-25
CHI11-04-01-80 | C04/01-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 08-Mar-25 |  | 10-Mar-25
CHI11-04-01-85 | C04/01-DH- Overhead R/I - Mechanical | [5 empty] | 11-Mar-25 |  | 12-Mar-25
CHI11-04-01-90 | C04/01-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 11-Mar-25 |  | 12-Mar-25
CHI11-04-01-95 | C04/01-Elec Rm- Finish Dry-Wall | [5 empty] | 11-Mar-25 |  | 12-Mar-25
CHI11-04-02-10 | C04/02-DH- Layout Framing | [5 empty] | 05-Mar-25 |  | 05-Mar-25
CHI11-04-02-100 | C04/02-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 19-Mar-25 |  | 19-Mar-25
CHI11-04-02-105 | C04/02-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 19-Mar-25 |  | 20-Mar-25
CHI11-04-02-110 | C04/02-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 19-Mar-25 |  | 21-Mar-25
CHI11-04-02-115 | C04/02-DH- Paint Dry-Wall | [5 empty] | 20-Mar-25 |  | 24-Mar-25
CHI11-04-02-120 | C04/02-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 20-Mar-25 |  | 21-Mar-25
CHI11-04-02-125 | C04/02-Elec Rm- Paint Dry-Wall | [5 empty] | 21-Mar-25 |  | 24-Mar-25
CHI11-04-02-130 | C04/02-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 24-Mar-25 |  | 29-Mar-25
CHI11-04-02-135 | C04/02-DH- Install Screen Mesh + Caulking | [5 empty] | 25-Mar-25 |  | 27-Mar-25
CHI11-04-02-140 | C04/02-Elec Rm- General Cleaning | [5 empty] | 25-Mar-25 |  | 25-Mar-25
CHI11-04-02-145 | C04/02-Elec Rm- Set Electrical Equipments | [5 empty] | 26-Mar-25 |  | 29-Mar-25
CHI11-04-02-15 | C04/02-DH- Install Framing | [5 empty] | 06-Mar-25 |  | 08-Mar-25
CHI11-04-02-150 | C04/02-DH- Install Secondary Steel | [5 empty] | 28-Mar-25 |  | 29-Mar-25
CHI11-04-02-155 | C04/02-DH- Paint Secondary Steel | [5 empty] | 31-Mar-25 |  | 01-Apr-25
CHI11-04-02-160 | C04/02-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 31-Mar-25 |  | 05-Apr-25
CHI11-04-02-165 | C04/02-DH- General Cleaning | [5 empty] | 02-Apr-25 |  | 02-Apr-25
CHI11-04-02-170 | C04/02-DH- Install Ceiling Grid | [5 empty] | 02-Apr-25 |  | 05-Apr-25
CHI11-04-02-175 | C04/02-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 04-Apr-25 |  | 05-Apr-25
CHI11-04-02-180 | C04/02-DH- Install Perimeter Cable Trays | [5 empty] | 07-Apr-25 |  | 10-Apr-25
CHI11-04-02-185 | C04/02-DH- Assemble HACs [Qty - 5] | [5 empty] | 07-Apr-25 |  | 11-Apr-25
CHI11-04-02-190 | C04/02-Mech Gallery- Finish Dry-Wall | [5 empty] | 07-Apr-25 |  | 08-Apr-25
CHI11-04-02-195 | C04/02-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 07-Apr-25 |  | 07-Apr-25
CHI11-04-02-20 | C04/02-DH- In-Wall R/I | [5 empty] | 10-Mar-25 |  | 12-Mar-25
CHI11-04-02-200 | C04/02-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 08-Apr-25 |  | 11-Apr-25
CHI11-04-02-205 | C04/02-DH- Install Busways on HAC Arms | [5 empty] | 09-Apr-25 |  | 15-Apr-25
CHI11-04-02-210 | C04/02-Mech Gallery- Paint Dry-Wall | [5 empty] | 09-Apr-25 |  | 10-Apr-25
CHI11-04-02-215 | C04/02-DH- Install Device Tiles | [5 empty] | 11-Apr-25 |  | 14-Apr-25
CHI11-04-02-220 | C04/02-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 11-Apr-25 |  | 17-Apr-25
CHI11-04-02-225 | C04/02-DH- Set PDUs | [5 empty] | 11-Apr-25 |  | 16-Apr-25
CHI11-04-02-230 | C04/02-Mech Gallery- General Cleaning | [5 empty] | 11-Apr-25 |  | 15-Apr-25
CHI11-04-02-235 | C04/02-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 14-Apr-25 |  | 15-Apr-25
CHI11-04-02-240 | C04/02-Mech Gallery- Install BAS Equipments | [5 empty] | 14-Apr-25 |  | 24-Apr-25
CHI11-04-02-245 | C04/02-Mech Gallery- Set Mechanical Equipments | [5 empty] | 16-Apr-25 |  | 19-Apr-25
CHI11-04-02-25 | C04/02-Elec Rm- Install Framing | [5 empty] | 10-Mar-25 |  | 11-Mar-25
CHI11-04-02-250 | C04/02-DH- Raise HACs | [5 empty] | 18-Apr-25 |  | 22-Apr-25
CHI11-04-02-255 | C04/02-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 21-Apr-25 |  | 05-May-25
CHI11-04-02-260 | C04/02-DH- Detail HACs | [5 empty] | 23-Apr-25 |  | 26-Apr-25
CHI11-04-02-265 | C04/02-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 23-Apr-25 |  | 25-Apr-25
CHI11-04-02-270 | C04/02-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 25-Apr-25 |  | 05-May-25
CHI11-04-02-275 | C04/02-DH- Install Conduits PDU to Cable Trays | [5 empty] | 26-Apr-25 |  | 29-Apr-25
CHI11-04-02-280 | C04/02- Punchlist | [5 empty] | 31-May-25 |  | 11-Jun-25
CHI11-04-02-285 | C04/02-DH- Pull Feeders from PDUs to Busways | [5 empty] | 30-Apr-25 |  | 06-May-25
CHI11-04-02-290 | C04/02-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | [5 empty] | 01-May-25 |  | 14-May-25
CHI11-04-02-295 | C04/02-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 06-May-25 |  | 09-May-25
CHI11-04-02-30 | C04/02-Elec Rm- In-Wall R/I | [5 empty] | 12-Mar-25 |  | 13-Mar-25
CHI11-04-02-300 | C04/02-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 15-May-25 |  | 19-May-25
CHI11-04-02-305 | C04/02-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | [5 empty] | 15-May-25 |  | 27-May-25
CHI11-04-02-310 | C04/02-DH- Terminate PDUs | [5 empty] | 28-May-25 |  | 30-May-25
CHI11-04-02-315 | C04/02-L2Cx- Yellow Tags | [5 empty] | 31-May-25 |  | 24-Jun-25
CHI11-04-02-320 | C04/02-L3Cx- Control Power Checks | [5 empty] | 25-Jun-25 |  | 03-Jul-25
CHI11-04-02-325 | C04/02-L3Cx- EPMS Point to Point Checks | [5 empty] | 07-Jul-25 |  | 15-Jul-25
CHI11-04-02-330 | C04/02-L3Cx- FTE Energizations [480v] | [5 empty] | 16-Jul-25 |  | 19-Jul-25
CHI11-04-02-335 | C04/02-L3Cx- Startups | [5 empty] | 21-Jul-25 |  | 04-Aug-25
CHI11-04-02-340 | C04/02-L3Cx- Loadbanking | [5 empty] | 05-Aug-25 |  | 08-Aug-25
CHI11-04-02-35 | C04/02-DH- Overhead R/I - Fire Protection | [5 empty] | 13-Mar-25 |  | 15-Mar-25
CHI11-04-02-40 | C04/02-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 13-Mar-25 |  | 15-Mar-25
CHI11-04-02-45 | C04/02-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 14-Mar-25 |  | 15-Mar-25
CHI11-04-02-50 | C04/02-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 14-Mar-25 |  | 18-Mar-25
CHI11-04-02-55 | C04/02-DH- Overhead R/I - Fire Alarm | [5 empty] | 17-Mar-25 |  | 19-Mar-25
CHI11-04-02-60 | C04/02-DH- Overhead R/I - Electrical | [5 empty] | 17-Mar-25 |  | 20-Mar-25
CHI11-04-02-65 | C04/02-DH- Finish Dry-Wall | [5 empty] | 17-Mar-25 |  | 19-Mar-25
CHI11-04-02-70 | C04/02-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 17-Mar-25 |  | 18-Mar-25
CHI11-04-02-75 | C04/02-Elec Rm- Overhead R/I - Electrical | [5 empty] | 17-Mar-25 |  | 19-Mar-25
CHI11-04-02-80 | C04/02-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 17-Mar-25 |  | 18-Mar-25
CHI11-04-02-85 | C04/02-DH- Overhead R/I - Mechanical | [5 empty] | 19-Mar-25 |  | 20-Mar-25
CHI11-04-02-90 | C04/02-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 19-Mar-25 |  | 20-Mar-25
CHI11-04-02-95 | C04/02-Elec Rm- Finish Dry-Wall | [5 empty] | 19-Mar-25 |  | 20-Mar-25
CHI11-04-03-10 | C04/03-DH- Layout Framing | [5 empty] | 28-Mar-25 |  | 28-Mar-25
CHI11-04-03-100 | C04/03-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 11-Apr-25 |  | 11-Apr-25
CHI11-04-03-105 | C04/03-Mech Gallery- - Overhead R/I - Fire Alarm | [5 empty] | 11-Apr-25 |  | 14-Apr-25
CHI11-04-03-110 | C04/03-Mech Gallery- - Overhead R/I - Electrical | [5 empty] | 11-Apr-25 |  | 15-Apr-25
CHI11-04-03-115 | C04/03-DH- Paint Dry-Wall | [5 empty] | 14-Apr-25 |  | 16-Apr-25
CHI11-04-03-120 | C04/03-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 14-Apr-25 |  | 15-Apr-25
CHI11-04-03-125 | C04/03-Elec Rm- Paint Dry-Wall | [5 empty] | 15-Apr-25 |  | 16-Apr-25
CHI11-04-03-130 | C04/03-Mech Gallery- - Overhead R/I - Mechanical | [5 empty] | 16-Apr-25 |  | 22-Apr-25
CHI11-04-03-135 | C04/03-DH- Install Screen Mesh + Caulking | [5 empty] | 17-Apr-25 |  | 19-Apr-25
CHI11-04-03-140 | C04/03-Elec Rm- General Cleaning | [5 empty] | 17-Apr-25 |  | 17-Apr-25
CHI11-04-03-145 | C04/03-Elec Rm- Set Electrical Equipments | [5 empty] | 18-Apr-25 |  | 22-Apr-25
CHI11-04-03-15 | C04/03-DH- Install Framing | [5 empty] | 29-Mar-25 |  | 01-Apr-25
CHI11-04-03-150 | C04/03-DH- Install Secondary Steel | [5 empty] | 21-Apr-25 |  | 22-Apr-25
CHI11-04-03-155 | C04/03-DH- Paint Secondary Steel | [5 empty] | 23-Apr-25 |  | 24-Apr-25
CHI11-04-03-160 | C04/03-Mech Gallery- - Overhead R/I - Plumbing | [5 empty] | 23-Apr-25 |  | 29-Apr-25
CHI11-04-03-165 | C04/03-DH- General Cleaning | [5 empty] | 25-Apr-25 |  | 25-Apr-25
CHI11-04-03-170 | C04/03-DH- Install Ceiling Grid | [5 empty] | 25-Apr-25 |  | 29-Apr-25
CHI11-04-03-175 | C04/03-Mech Gallery- - Install Drywall [Mech Gallery] | [5 empty] | 28-Apr-25 |  | 29-Apr-25
CHI11-04-03-180 | C04/03-DH- Install Perimeter Cable Trays | [5 empty] | 30-Apr-25 |  | 05-May-25
CHI11-04-03-185 | C04/03-DH- Assemble HACs [Qty - 5] | [5 empty] | 30-Apr-25 |  | 06-May-25
CHI11-04-03-190 | C04/03-Mech Gallery- - Finish Dry-Wall | [5 empty] | 30-Apr-25 |  | 01-May-25
CHI11-04-03-195 | C04/03-Mech Gallery- - Drop Cable Tray [Hanging Rods] | [5 empty] | 30-Apr-25 |  | 30-Apr-25
CHI11-04-03-20 | C04/03-DH- In-Wall R/I | [5 empty] | 02-Apr-25 |  | 04-Apr-25
CHI11-04-03-200 | C04/03-Mech Gallery- - Install Ceiling Grid + Device Tiles | [5 empty] | 01-May-25 |  | 06-May-25
CHI11-04-03-205 | C04/03-DH- Install Busways on HAC Arms | [5 empty] | 02-May-25 |  | 08-May-25
CHI11-04-03-210 | C04/03-Mech Gallery- - Paint Dry-Wall | [5 empty] | 02-May-25 |  | 05-May-25
CHI11-04-03-215 | C04/03-DH- Install Device Tiles | [5 empty] | 06-May-25 |  | 07-May-25
CHI11-04-03-220 | C04/03-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 06-May-25 |  | 10-May-25
CHI11-04-03-225 | C04/03-DH- Set PDUs | [5 empty] | 06-May-25 |  | 09-May-25
CHI11-04-03-230 | C04/03-Mech Gallery- - General Cleaning | [5 empty] | 06-May-25 |  | 08-May-25
CHI11-04-03-235 | C04/03-Mech Gallery- - Install Cable Trays / Pathways | [5 empty] | 07-May-25 |  | 08-May-25
CHI11-04-03-240 | C04/03-Mech Gallery- - Install BAS Equipments | [5 empty] | 07-May-25 |  | 17-May-25
CHI11-04-03-245 | C04/03-Mech Gallery- - Set Mechanical Equipments | [5 empty] | 09-May-25 |  | 13-May-25
CHI11-04-03-25 | C04/03-Elec Rm- Install Framing | [5 empty] | 02-Apr-25 |  | 03-Apr-25
CHI11-04-03-250 | C04/03-DH- Raise HACs | [5 empty] | 12-May-25 |  | 15-May-25
CHI11-04-03-255 | C04/03-Mech Gallery- - Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 14-May-25 |  | 28-May-25
CHI11-04-03-260 | C04/03-DH- Detail HACs | [5 empty] | 16-May-25 |  | 20-May-25
CHI11-04-03-265 | C04/03-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 16-May-25 |  | 19-May-25
CHI11-04-03-270 | C04/03-Mech Gallery- - Pull & Terminate BAS Equipments | [5 empty] | 19-May-25 |  | 28-May-25
CHI11-04-03-275 | C04/03-DH- Install Conduits PDU to Cable Trays | [5 empty] | 20-May-25 |  | 22-May-25
CHI11-04-03-280 | C04/03- Punchlist | [5 empty] | 22-Jul-25 |  | 02-Aug-25
CHI11-04-03-285 | C04/03-DH- Pull Feeders from PDUs to Busways | [5 empty] | 23-May-25 |  | 29-May-25
CHI11-04-03-290 | C04/03-Mech Gallery- - Terminate Mechanical Equipments | [5 empty] | 29-May-25 |  | 02-Jun-25
CHI11-04-03-295 | C04/03-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | [5 empty] | 24-Jun-25 |  | 08-Jul-25
CHI11-04-03-30 | C04/03-Elec Rm- In-Wall R/I | [5 empty] | 04-Apr-25 |  | 05-Apr-25
CHI11-04-03-300 | C04/03-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 09-Jul-25 |  | 12-Jul-25
CHI11-04-03-305 | C04/03-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | [5 empty] | 09-Jul-25 |  | 19-Jul-25
CHI11-04-03-310 | C04/03-DH- Terminate PDUs | [5 empty] | 18-Jul-25 |  | 21-Jul-25
CHI11-04-03-315 | C04/03-L2Cx- Yellow Tags | [5 empty] | 22-Jul-25 |  | 14-Aug-25
CHI11-04-03-320 | C04/03-L3Cx- Control Power Checks | [5 empty] | 06-Aug-25 |  | 14-Aug-25
CHI11-04-03-325 | C04/03-L3Cx- EPMS Point to Point Checks | [5 empty] | 15-Aug-25 |  | 25-Aug-25
CHI11-04-03-330 | C04/03-L3Cx- FTE Energizations [480v] | [5 empty] | 26-Aug-25 |  | 29-Aug-25
CHI11-04-03-335 | C04/03-L3Cx- Startups | [5 empty] | 30-Aug-25 |  | 15-Sep-25
CHI11-04-03-340 | C04/03-L3Cx- Loadbanking | [5 empty] | 16-Sep-25 |  | 19-Sep-25
CHI11-04-03-35 | C04/03-DH- Overhead R/I - Fire Protection | [5 empty] | 05-Apr-25 |  | 08-Apr-25
CHI11-04-03-40 | C04/03-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 05-Apr-25 |  | 08-Apr-25
CHI11-04-03-45 | C04/03-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 07-Apr-25 |  | 08-Apr-25
CHI11-04-03-50 | C04/03-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 07-Apr-25 |  | 10-Apr-25
CHI11-04-03-55 | C04/03-DH- Overhead R/I - Fire Alarm | [5 empty] | 09-Apr-25 |  | 11-Apr-25
CHI11-04-03-60 | C04/03-DH- Overhead R/I - Electrical | [5 empty] | 09-Apr-25 |  | 14-Apr-25
CHI11-04-03-65 | C04/03-DH- Finish Dry-Wall | [5 empty] | 09-Apr-25 |  | 11-Apr-25
CHI11-04-03-70 | C04/03-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 09-Apr-25 |  | 10-Apr-25
CHI11-04-03-75 | C04/03-Elec Rm- Overhead R/I - Electrical | [5 empty] | 09-Apr-25 |  | 11-Apr-25
CHI11-04-03-80 | C04/03-Mech Gallery- - Overhead R/I - Fire Protection | [5 empty] | 09-Apr-25 |  | 10-Apr-25
CHI11-04-03-85 | C04/03-DH- Overhead R/I - Mechanical | [5 empty] | 11-Apr-25 |  | 14-Apr-25
CHI11-04-03-90 | C04/03-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 11-Apr-25 |  | 14-Apr-25
CHI11-04-03-95 | C04/03-Elec Rm- Finish Dry-Wall | [5 empty] | 11-Apr-25 |  | 14-Apr-25
CHI11-04-04-10 | C04/04-DH-Layout Framing | [5 empty] | 15-Mar-25 |  | 15-Mar-25
CHI11-04-04-100 | C04/04-Elec Rm-Drop Cable Tray [Hanging Rods] | [5 empty] | 31-Mar-25 |  | 31-Mar-25
CHI11-04-04-105 | C04/04-Mech Gallery-Overhead R/I - Fire Alarm | [5 empty] | 31-Mar-25 |  | 01-Apr-25
CHI11-04-04-110 | C04/04-Mech Gallery-Overhead R/I - Electrical | [5 empty] | 31-Mar-25 |  | 02-Apr-25
CHI11-04-04-115 | C04/04-DH-Paint Dry-Wall | [5 empty] | 01-Apr-25 |  | 03-Apr-25
CHI11-04-04-120 | C04/04-Elec Rm-Install Cable Trays / Pathways | [5 empty] | 01-Apr-25 |  | 02-Apr-25
CHI11-04-04-125 | C04/04-Elec Rm-Paint Dry-Wall | [5 empty] | 02-Apr-25 |  | 03-Apr-25
CHI11-04-04-130 | C04/04-Mech Gallery-Overhead R/I - Mechanical | [5 empty] | 03-Apr-25 |  | 09-Apr-25
CHI11-04-04-135 | C04/04-DH-Install Screen Mesh + Caulking | [5 empty] | 04-Apr-25 |  | 07-Apr-25
CHI11-04-04-140 | C04/04-Elec Rm-General Cleaning | [5 empty] | 04-Apr-25 |  | 04-Apr-25
CHI11-04-04-145 | C04/04-Elec Rm-Set Electrical Equipments | [5 empty] | 05-Apr-25 |  | 09-Apr-25
CHI11-04-04-15 | C04/04-DH-Install Framing | [5 empty] | 17-Mar-25 |  | 19-Mar-25
CHI11-04-04-150 | C04/04-DH-Install Secondary Steel | [5 empty] | 08-Apr-25 |  | 09-Apr-25
CHI11-04-04-155 | C04/04-DH-Paint Secondary Steel | [5 empty] | 10-Apr-25 |  | 11-Apr-25
CHI11-04-04-160 | C04/04-Mech Gallery-Overhead R/I - Plumbing | [5 empty] | 10-Apr-25 |  | 17-Apr-25
CHI11-04-04-165 | C04/04-DH-General Cleaning | [5 empty] | 14-Apr-25 |  | 14-Apr-25
CHI11-04-04-170 | C04/04-DH-Install Ceiling Grid | [5 empty] | 14-Apr-25 |  | 17-Apr-25
CHI11-04-04-175 | C04/04-Mech Gallery-Install Drywall [Mech Gallery] | [5 empty] | 16-Apr-25 |  | 17-Apr-25
CHI11-04-04-180 | C04/04-DH-Install Perimeter Cable Trays | [5 empty] | 18-Apr-25 |  | 22-Apr-25
CHI11-04-04-185 | C04/04-DH-Assemble HACs [Qty - 5] | [5 empty] | 18-Apr-25 |  | 23-Apr-25
CHI11-04-04-190 | C04/04-Mech Gallery-Finish Dry-Wall | [5 empty] | 18-Apr-25 |  | 19-Apr-25
CHI11-04-04-195 | C04/04-Mech Gallery-Drop Cable Tray [Hanging Rods] | [5 empty] | 18-Apr-25 |  | 18-Apr-25
CHI11-04-04-20 | C04/04-DH-In-Wall R/I | [5 empty] | 20-Mar-25 |  | 24-Mar-25
CHI11-04-04-200 | C04/04-Mech Gallery-Install Ceiling Grid + Device Tiles | [5 empty] | 19-Apr-25 |  | 23-Apr-25
CHI11-04-04-205 | C04/04-DH-Install Busways on HAC Arms | [5 empty] | 21-Apr-25 |  | 25-Apr-25
CHI11-04-04-210 | C04/04-Mech Gallery-Paint Dry-Wall | [5 empty] | 21-Apr-25 |  | 22-Apr-25
CHI11-04-04-215 | C04/04-DH-Install Device Tiles | [5 empty] | 23-Apr-25 |  | 24-Apr-25
CHI11-04-04-220 | C04/04-DH-Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 23-Apr-25 |  | 28-Apr-25
CHI11-04-04-225 | C04/04-DH-Set PDUs | [5 empty] | 23-Apr-25 |  | 26-Apr-25
CHI11-04-04-230 | C04/04-Mech Gallery-General Cleaning | [5 empty] | 23-Apr-25 |  | 25-Apr-25
CHI11-04-04-235 | C04/04-Mech Gallery-Install Cable Trays / Pathways | [5 empty] | 24-Apr-25 |  | 25-Apr-25
CHI11-04-04-240 | C04/04-Mech Gallery-Install BAS Equipments | [5 empty] | 24-Apr-25 |  | 06-May-25
CHI11-04-04-245 | C04/04-Mech Gallery-Set Mechanical Equipments | [5 empty] | 26-Apr-25 |  | 30-Apr-25
CHI11-04-04-25 | C04/04-Elec Rm-Install Framing | [5 empty] | 20-Mar-25 |  | 21-Mar-25
CHI11-04-04-250 | C04/04-DH-Raise HACs | [5 empty] | 29-Apr-25 |  | 02-May-25
CHI11-04-04-255 | C04/04-Mech Gallery-Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 01-May-25 |  | 15-May-25
CHI11-04-04-260 | C04/04-DH-Detail HACs | [5 empty] | 05-May-25 |  | 08-May-25
CHI11-04-04-265 | C04/04-DH-Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 05-May-25 |  | 07-May-25
CHI11-04-04-270 | C04/04-Mech Gallery-Pull & Terminate BAS Equipments | [5 empty] | 07-May-25 |  | 15-May-25
CHI11-04-04-275 | C04/04-DH-Install Conduits PDU to Cable Trays | [5 empty] | 08-May-25 |  | 10-May-25
CHI11-04-04-280 | C04/04- Punchlist | [5 empty] | 27-Jun-25 |  | 10-Jul-25
CHI11-04-04-285 | C04/04-DH-Pull Feeders from PDUs to Busways | [5 empty] | 12-May-25 |  | 16-May-25
CHI11-04-04-290 | C04/04-Mech Gallery-Terminate Mechanical Equipments | [5 empty] | 16-May-25 |  | 20-May-25
CHI11-04-04-295 | C04/04-Elec Rm-Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | [5 empty] | 28-May-25 |  | 09-Jun-25
CHI11-04-04-30 | C04/04-Elec Rm-In-Wall R/I | [5 empty] | 24-Mar-25 |  | 25-Mar-25
CHI11-04-04-300 | C04/04-Elec Rm-Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 10-Jun-25 |  | 13-Jun-25
CHI11-04-04-305 | C04/04-Elec Rm-Pull Feeders from Electrical Room to PDUs Pull Crew 2 | [5 empty] | 10-Jun-25 |  | 23-Jun-25
CHI11-04-04-310 | C04/04-DH-Terminate PDUs | [5 empty] | 24-Jun-25 |  | 26-Jun-25
CHI11-04-04-315 | C04/04-L2Cx- Yellow Tags | [5 empty] | 27-Jun-25 |  | 22-Jul-25
CHI11-04-04-320 | C04/04-L3Cx- Control Power Checks | [5 empty] | 18-Jul-25 |  | 28-Jul-25
CHI11-04-04-325 | C04/04-L3Cx- EPMS Point to Point Checks | [5 empty] | 29-Jul-25 |  | 06-Aug-25
CHI11-04-04-330 | C04/04-L3Cx- FTE Energizations [480v] | [5 empty] | 07-Aug-25 |  | 11-Aug-25
CHI11-04-04-335 | C04/04-L3Cx- Startups | [5 empty] | 12-Aug-25 |  | 26-Aug-25
CHI11-04-04-340 | C04/04-L3Cx- Loadbanking | [5 empty] | 27-Aug-25 |  | 30-Aug-25
CHI11-04-04-35 | C04/04-DH-Overhead R/I - Fire Protection | [5 empty] | 25-Mar-25 |  | 27-Mar-25
CHI11-04-04-40 | C04/04-DH-Install Drywall (One Side - Facing DH) | [5 empty] | 25-Mar-25 |  | 27-Mar-25
CHI11-04-04-45 | C04/04-Elec Rm-Overhead R/I - Fire Protection | [5 empty] | 26-Mar-25 |  | 27-Mar-25
CHI11-04-04-50 | C04/04-Elec Rm-Install Drywall [Elec + Battery Rooms] | [5 empty] | 26-Mar-25 |  | 29-Mar-25
CHI11-04-04-55 | C04/04-DH-Overhead R/I - Fire Alarm | [5 empty] | 28-Mar-25 |  | 31-Mar-25
CHI11-04-04-60 | C04/04-DH-Overhead R/I - Electrical | [5 empty] | 28-Mar-25 |  | 01-Apr-25
CHI11-04-04-65 | C04/04-DH-Finish Dry-Wall | [5 empty] | 28-Mar-25 |  | 31-Mar-25
CHI11-04-04-70 | C04/04-Elec Rm-Overhead R/I - Fire Alarm | [5 empty] | 28-Mar-25 |  | 29-Mar-25
CHI11-04-04-75 | C04/04-Elec Rm-Overhead R/I - Electrical | [5 empty] | 28-Mar-25 |  | 31-Mar-25
CHI11-04-04-80 | C04/04-Mech Gallery-Overhead R/I - Fire Protection | [5 empty] | 28-Mar-25 |  | 29-Mar-25
CHI11-04-04-85 | C04/04-DH-Overhead R/I - Mechanical | [5 empty] | 31-Mar-25 |  | 01-Apr-25
CHI11-04-04-90 | C04/04-DH-Drop Cable Tray [Hanging Rods] | [5 empty] | 31-Mar-25 |  | 01-Apr-25
CHI11-04-04-95 | C04/04-Elec Rm-Finish Dry-Wall | [5 empty] | 31-Mar-25 |  | 01-Apr-25
CHI11-04-C&S-10 | C04- Install Primary Steel | [5 empty] | 01-Nov-2024 |  | 20-Nov-24
CHI11-04-C&S-15 | C04- Install Roof Panels | [5 empty] | 16-Dec-24 |  | 31-Dec-24
CHI11-04-C&S-20 | C04- UG MEP Work AMS/Gibson | [5 empty] | 04-Dec-24 |  | 27-Dec-24
CHI11-04-C&S-25 | C04- Install Exterior Wall Panels | [5 empty] | 21-Nov-24 |  | 14-Dec-24
CHI11-04-C&S-30 | C04- Prep / Place SOG | [5 empty] | 30-Dec-24 |  | 10-Jan-25
CHI11-04-C&S-35 | C04- Install Louvers & Dampers | [5 empty] | 07-Jan-25 |  | 25-Jan-25
CHI11-04-C&S-40 | C04- Install Misc. Metals (Trims, Gutters, Catwalks) | [5 empty] | 11-Jan-25 |  | 30-Jan-25
CHI11-04-L4-10 | C04-L4Cx- Testing <MSFT Duration> | [5 empty] | 20-Sep-25 |  | 16-Oct-25
CHI11-04-L5-10 | C04-L5Cx- Testing <MSFT Duration> | [5 empty] | 17-Oct-25 |  | 20-Oct-25
CHI11-04-YARD-10 | C04/Yard- Build Equipment Pads for XFMs | [5 empty] | 21-Feb-25 |  | 04-Mar-25
CHI11-04-YARD-15 | C04/Yard- Build Equipment Pads for UPMs | [5 empty] | 05-Mar-25 |  | 14-Mar-25
CHI11-04-YARD-20 | C04/Yard- Build Equipment Pads for UMSs | [5 empty] | 15-Mar-25 |  | 26-Mar-25
CHI11-04-YARD-25 | C04/Yard- Build Equipment Pads for Generators | [5 empty] | 27-Mar-25 |  | 05-Apr-25
CHI11-04-YARD-30 | C04/Yard- Install XFMs | [5 empty] | 02-Apr-25 |  | 15-Apr-25
CHI11-04-YARD-35 | C04/Yard- Install UPMs | [5 empty] | 02-Apr-25 |  | 15-Apr-25
CHI11-04-YARD-40 | C04/Yard- Install UMSs | [5 empty] | 02-Apr-25 |  | 15-Apr-25
CHI11-04-YARD-45 | C04/Yard- Install Generators | [5 empty] | 11-Apr-25 |  | 24-Apr-25
CHI11-04-YARD-50 | C04/Yard- MV Cable Pulling & Terminating to Cell 1 | [5 empty] | 25-Apr-25 |  | 05-May-25
CHI11-04-YARD-55 | C04/Yard- MV Cable Pulling & Terminating to Cell 2 | [5 empty] | 06-May-25 |  | 14-May-25
CHI11-04-YARD-60 | C04/Yard- MV Cable Pulling & Terminating to Cell 4 | [5 empty] | 15-May-25 |  | 23-May-25
CHI11-04-YARD-65 | C04/Yard- MV Cable Pulling & Terminating to Cell 3 | [5 empty] | 27-May-25 |  | 04-Jun-25
CHI11-05-01-10 | C05/01-DH- Layout Framing | [5 empty] | 31-Mar-25 |  | 31-Mar-25
CHI11-05-01-100 | C05/01-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 15-Apr-25 |  | 15-Apr-25
CHI11-05-01-105 | C05/01-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 15-Apr-25 |  | 16-Apr-25
CHI11-05-01-110 | C05/01-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 15-Apr-25 |  | 17-Apr-25
CHI11-05-01-115 | C05/01-DH- Paint Dry-Wall | [5 empty] | 16-Apr-25 |  | 18-Apr-25
CHI11-05-01-120 | C05/01-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 16-Apr-25 |  | 17-Apr-25
CHI11-05-01-125 | C05/01-Elec Rm- Paint Dry-Wall | [5 empty] | 17-Apr-25 |  | 18-Apr-25
CHI11-05-01-130 | C05/01-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 18-Apr-25 |  | 24-Apr-25
CHI11-05-01-135 | C05/01-DH- Install Screen Mesh + Caulking | [5 empty] | 19-Apr-25 |  | 22-Apr-25
CHI11-05-01-140 | C05/01-Elec Rm- General Cleaning | [5 empty] | 19-Apr-25 |  | 19-Apr-25
CHI11-05-01-145 | C05/01-Elec Rm- Set Electrical Equipments | [5 empty] | 21-Apr-25 |  | 01-May-25
CHI11-05-01-15 | C05/01-DH- Install Framing | [5 empty] | 01-Apr-25 |  | 03-Apr-25
CHI11-05-01-150 | C05/01-DH- Install Secondary Steel | [5 empty] | 23-Apr-25 |  | 24-Apr-25
CHI11-05-01-155 | C05/01-DH- Paint Secondary Steel | [5 empty] | 25-Apr-25 |  | 26-Apr-25
CHI11-05-01-160 | C05/01-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 25-Apr-25 |  | 01-May-25
CHI11-05-01-165 | C05/01-DH- General Cleaning | [5 empty] | 28-Apr-25 |  | 28-Apr-25
CHI11-05-01-170 | C05/01-DH- Install Ceiling Grid | [5 empty] | 28-Apr-25 |  | 01-May-25
CHI11-05-01-175 | C05/01-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 30-Apr-25 |  | 01-May-25
CHI11-05-01-180 | C05/01-DH- Install Perimeter Cable Trays | [5 empty] | 02-May-25 |  | 07-May-25
CHI11-05-01-185 | C05/01-DH- Assemble HACs [Qty - 5] | [5 empty] | 02-May-25 |  | 08-May-25
CHI11-05-01-190 | C05/01-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | [5 empty] | 02-May-25 |  | 15-May-25
CHI11-05-01-195 | C05/01-Mech Gallery- Finish Dry-Wall | [5 empty] | 02-May-25 |  | 05-May-25
CHI11-05-01-20 | C05/01-DH- In-Wall R/I | [5 empty] | 04-Apr-25 |  | 07-Apr-25
CHI11-05-01-200 | C05/01-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 02-May-25 |  | 02-May-25
CHI11-05-01-205 | C05/01-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 05-May-25 |  | 08-May-25
CHI11-05-01-210 | C05/01-DH- Install Busways on HAC Arms | [5 empty] | 06-May-25 |  | 10-May-25
CHI11-05-01-215 | C05/01-Mech Gallery- Paint Dry-Wall | [5 empty] | 06-May-25 |  | 07-May-25
CHI11-05-01-220 | C05/01-DH- Install Device Tiles | [5 empty] | 08-May-25 |  | 09-May-25
CHI11-05-01-225 | C05/01-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 08-May-25 |  | 13-May-25
CHI11-05-01-230 | C05/01-DH- Set PDUs | [5 empty] | 08-May-25 |  | 12-May-25
CHI11-05-01-235 | C05/01-Mech Gallery- General Cleaning | [5 empty] | 08-May-25 |  | 10-May-25
CHI11-05-01-240 | C05/01-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 09-May-25 |  | 10-May-25
CHI11-05-01-245 | C05/01-Mech Gallery- Install BAS Equipments | [5 empty] | 09-May-25 |  | 20-May-25
CHI11-05-01-25 | C05/01-Elec Rm- Install Framing | [5 empty] | 04-Apr-25 |  | 05-Apr-25
CHI11-05-01-250 | C05/01-Mech Gallery- Set Mechanical Equipments | [5 empty] | 12-May-25 |  | 15-May-25
CHI11-05-01-255 | C05/01-DH- Raise HACs | [5 empty] | 14-May-25 |  | 17-May-25
CHI11-05-01-260 | C05/01-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 16-May-25 |  | 20-May-25
CHI11-05-01-265 | C05/01-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | [5 empty] | 16-May-25 |  | 29-May-25
CHI11-05-01-270 | C05/01-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 16-May-25 |  | 30-May-25
CHI11-05-01-275 | C05/01-DH- Detail HACs | [5 empty] | 19-May-25 |  | 22-May-25
CHI11-05-01-280 | C05/01-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 19-May-25 |  | 21-May-25
CHI11-05-01-285 | C05/01-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 21-May-25 |  | 30-May-25
CHI11-05-01-290 | C05/01-DH- Install Conduits PDU to Cable Trays | [5 empty] | 22-May-25 |  | 23-May-25
CHI11-05-01-295 | C05/01-Punchlist | [5 empty] | 05-Jun-25 |  | 17-Jun-25
CHI11-05-01-30 | C05/01-Elec Rm- In-Wall R/I | [5 empty] | 07-Apr-25 |  | 08-Apr-25
CHI11-05-01-300 | C05/01-DH- Pull Feeders from PDUs to Busways | [5 empty] | 27-May-25 |  | 31-May-25
CHI11-05-01-305 | C05/01-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 31-May-25 |  | 04-Jun-25
CHI11-05-01-310 | C05/01-DH- Terminate PDUs | [5 empty] | 02-Jun-25 |  | 04-Jun-25
CHI11-05-01-315 | C05/01-L2Cx- Yellow Tags | [5 empty] | 05-Jun-25 |  | 28-Jun-25
CHI11-05-01-320 | C05/01-L3Cx- Control Power Checks | [5 empty] | 19-Jul-25 |  | 29-Jul-25
CHI11-05-01-325 | C05/01-L3Cx- EPMS Point to Point Checks | [5 empty] | 30-Jul-25 |  | 07-Aug-25
CHI11-05-01-330 | C05/01-L3Cx- FTE Energizations [480v] | [5 empty] | 08-Aug-25 |  | 12-Aug-25
CHI11-05-01-335 | C05/01-L3Cx- Startups | [5 empty] | 13-Aug-25 |  | 27-Aug-25
CHI11-05-01-340 | C05/01-L3Cx- Loadbanking | [5 empty] | 28-Aug-25 |  | 02-Sep-25
CHI11-05-01-35 | C05/01-DH- Overhead R/I - Fire Protection | [5 empty] | 08-Apr-25 |  | 10-Apr-25
CHI11-05-01-40 | C05/01-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 08-Apr-25 |  | 10-Apr-25
CHI11-05-01-45 | C05/01-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 09-Apr-25 |  | 10-Apr-25
CHI11-05-01-50 | C05/01-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 09-Apr-25 |  | 14-Apr-25
CHI11-05-01-55 | C05/01-DH- Overhead R/I - Fire Alarm | [5 empty] | 11-Apr-25 |  | 15-Apr-25
CHI11-05-01-60 | C05/01-DH- Overhead R/I - Electrical | [5 empty] | 11-Apr-25 |  | 16-Apr-25
CHI11-05-01-65 | C05/01-DH- Finish Dry-Wall | [5 empty] | 11-Apr-25 |  | 15-Apr-25
CHI11-05-01-70 | C05/01-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 11-Apr-25 |  | 14-Apr-25
CHI11-05-01-75 | C05/01-Elec Rm- Overhead R/I - Electrical | [5 empty] | 11-Apr-25 |  | 15-Apr-25
CHI11-05-01-80 | C05/01-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 11-Apr-25 |  | 14-Apr-25
CHI11-05-01-85 | C05/01-DH- Overhead R/I - Mechanical | [5 empty] | 15-Apr-25 |  | 16-Apr-25
CHI11-05-01-90 | C05/01-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 15-Apr-25 |  | 16-Apr-25
CHI11-05-01-95 | C05/01-Elec Rm- Finish Dry-Wall | [5 empty] | 15-Apr-25 |  | 16-Apr-25
CHI11-05-02-10 | C05/02-DH- Layout Framing | [5 empty] | 08-Apr-25 |  | 08-Apr-25
CHI11-05-02-100 | C05/02-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 23-Apr-25 |  | 23-Apr-25
CHI11-05-02-105 | C05/02-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 23-Apr-25 |  | 24-Apr-25
CHI11-05-02-110 | C05/02-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 23-Apr-25 |  | 25-Apr-25
CHI11-05-02-115 | C05/02-DH- Paint Dry-Wall | [5 empty] | 24-Apr-25 |  | 26-Apr-25
CHI11-05-02-120 | C05/02-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 24-Apr-25 |  | 25-Apr-25
CHI11-05-02-125 | C05/02-Elec Rm- Paint Dry-Wall | [5 empty] | 25-Apr-25 |  | 26-Apr-25
CHI11-05-02-130 | C05/02-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 26-Apr-25 |  | 02-May-25
CHI11-05-02-135 | C05/02-DH- Install Screen Mesh + Caulking | [5 empty] | 28-Apr-25 |  | 30-Apr-25
CHI11-05-02-140 | C05/02-Elec Rm- General Cleaning | [5 empty] | 28-Apr-25 |  | 28-Apr-25
CHI11-05-02-145 | C05/02-Elec Rm- Set Electrical Equipments | [5 empty] | 29-Apr-25 |  | 02-May-25
CHI11-05-02-15 | C05/02-DH- Install Framing | [5 empty] | 09-Apr-25 |  | 11-Apr-25
CHI11-05-02-150 | C05/02-DH- Install Secondary Steel | [5 empty] | 01-May-25 |  | 02-May-25
CHI11-05-02-155 | C05/02-DH- Paint Secondary Steel | [5 empty] | 05-May-25 |  | 06-May-25
CHI11-05-02-160 | C05/02-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 05-May-25 |  | 10-May-25
CHI11-05-02-165 | C05/02-DH- General Cleaning | [5 empty] | 07-May-25 |  | 07-May-25
CHI11-05-02-170 | C05/02-DH- Install Ceiling Grid | [5 empty] | 07-May-25 |  | 10-May-25
CHI11-05-02-175 | C05/02-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 09-May-25 |  | 10-May-25
CHI11-05-02-180 | C05/02-DH- Install Perimeter Cable Trays | [5 empty] | 12-May-25 |  | 15-May-25
CHI11-05-02-185 | C05/02-DH- Assemble HACs [Qty - 5] | [5 empty] | 12-May-25 |  | 16-May-25
CHI11-05-02-190 | C05/02-Mech Gallery- Finish Dry-Wall | [5 empty] | 12-May-25 |  | 13-May-25
CHI11-05-02-195 | C05/02-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 12-May-25 |  | 12-May-25
CHI11-05-02-20 | C05/02-DH- In-Wall R/I | [5 empty] | 14-Apr-25 |  | 16-Apr-25
CHI11-05-02-200 | C05/02-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 13-May-25 |  | 16-May-25
CHI11-05-02-205 | C05/02-DH- Install Busways on HAC Arms | [5 empty] | 14-May-25 |  | 19-May-25
CHI11-05-02-210 | C05/02-Mech Gallery- Paint Dry-Wall | [5 empty] | 14-May-25 |  | 15-May-25
CHI11-05-02-215 | C05/02-DH- Install Device Tiles | [5 empty] | 16-May-25 |  | 17-May-25
CHI11-05-02-220 | C05/02-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 16-May-25 |  | 21-May-25
CHI11-05-02-225 | C05/02-DH- Set PDUs | [5 empty] | 16-May-25 |  | 20-May-25
CHI11-05-02-230 | C05/02-Mech Gallery- General Cleaning | [5 empty] | 16-May-25 |  | 19-May-25
CHI11-05-02-235 | C05/02-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 17-May-25 |  | 19-May-25
CHI11-05-02-240 | C05/02-Mech Gallery- Install BAS Equipments | [5 empty] | 17-May-25 |  | 29-May-25
CHI11-05-02-245 | C05/02-Mech Gallery- Set Mechanical Equipments | [5 empty] | 20-May-25 |  | 23-May-25
CHI11-05-02-25 | C05/02-Elec Rm- Install Framing | [5 empty] | 14-Apr-25 |  | 15-Apr-25
CHI11-05-02-250 | C05/02-DH- Raise HACs | [5 empty] | 22-May-25 |  | 27-May-25
CHI11-05-02-255 | C05/02-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 27-May-25 |  | 07-Jun-25
CHI11-05-02-260 | C05/02-DH- Detail HACs | [5 empty] | 28-May-25 |  | 31-May-25
CHI11-05-02-265 | C05/02-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 28-May-25 |  | 30-May-25
CHI11-05-02-270 | C05/02-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 1 | [5 empty] | 30-May-25 |  | 11-Jun-25
CHI11-05-02-275 | C05/02-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 30-May-25 |  | 07-Jun-25
CHI11-05-02-280 | C05/02-DH- Install Conduits PDU to Cable Trays | [5 empty] | 31-May-25 |  | 03-Jun-25
CHI11-05-02-285 | C05/02- Punchlist | [5 empty] | 28-Jun-25 |  | 11-Jul-25
CHI11-05-02-290 | C05/02-DH- Pull Feeders from PDUs to Busways | [5 empty] | 04-Jun-25 |  | 09-Jun-25
CHI11-05-02-295 | C05/02-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 09-Jun-25 |  | 12-Jun-25
CHI11-05-02-30 | C05/02-Elec Rm- In-Wall R/I | [5 empty] | 16-Apr-25 |  | 17-Apr-25
CHI11-05-02-300 | C05/02-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 12-Jun-25 |  | 17-Jun-25
CHI11-05-02-305 | C05/02-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 1 | [5 empty] | 12-Jun-25 |  | 24-Jun-25
CHI11-05-02-310 | C05/02-DH- Terminate PDUs | [5 empty] | 25-Jun-25 |  | 27-Jun-25
CHI11-05-02-315 | C05/02-L2Cx- Yellow Tags | [5 empty] | 28-Jun-25 |  | 23-Jul-25
CHI11-05-02-320 | C05/02-L3Cx- Control Power Checks | [5 empty] | 24-Jul-25 |  | 02-Aug-25
CHI11-05-02-325 | C05/02-L3Cx- EPMS Point to Point Checks | [5 empty] | 04-Aug-25 |  | 12-Aug-25
CHI11-05-02-330 | C05/02-L3Cx- FTE Energizations [480v] | [5 empty] | 13-Aug-25 |  | 18-Aug-25
CHI11-05-02-335 | C05/02-L3Cx- Startups | [5 empty] | 19-Aug-25 |  | 02-Sep-25
CHI11-05-02-340 | C05/02-L3Cx- Loadbanking | [5 empty] | 03-Sep-25 |  | 08-Sep-25
CHI11-05-02-35 | C05/02-DH- Overhead R/I - Fire Protection | [5 empty] | 17-Apr-25 |  | 19-Apr-25
CHI11-05-02-40 | C05/02-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 17-Apr-25 |  | 19-Apr-25
CHI11-05-02-45 | C05/02-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 18-Apr-25 |  | 19-Apr-25
CHI11-05-02-50 | C05/02-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 18-Apr-25 |  | 22-Apr-25
CHI11-05-02-55 | C05/02-DH- Overhead R/I - Fire Alarm | [5 empty] | 21-Apr-25 |  | 23-Apr-25
CHI11-05-02-60 | C05/02-DH- Overhead R/I - Electrical | [5 empty] | 21-Apr-25 |  | 24-Apr-25
CHI11-05-02-65 | C05/02-DH- Finish Dry-Wall | [5 empty] | 21-Apr-25 |  | 23-Apr-25
CHI11-05-02-70 | C05/02-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 21-Apr-25 |  | 22-Apr-25
CHI11-05-02-75 | C05/02-Elec Rm- Overhead R/I - Electrical | [5 empty] | 21-Apr-25 |  | 23-Apr-25
CHI11-05-02-80 | C05/02-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 21-Apr-25 |  | 22-Apr-25
CHI11-05-02-85 | C05/02-DH- Overhead R/I - Mechanical | [5 empty] | 23-Apr-25 |  | 24-Apr-25
CHI11-05-02-90 | C05/02-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 23-Apr-25 |  | 24-Apr-25
CHI11-05-02-95 | C05/02-Elec Rm- Finish Dry-Wall | [5 empty] | 23-Apr-25 |  | 24-Apr-25
CHI11-05-03-10 | C05/03-DH- Layout Framing | [5 empty] | 01-May-25 |  | 01-May-25
CHI11-05-03-100 | C05/03-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 16-May-25 |  | 16-May-25
CHI11-05-03-105 | C05/03-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 16-May-25 |  | 17-May-25
CHI11-05-03-110 | C05/03-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 16-May-25 |  | 19-May-25
CHI11-05-03-115 | C05/03-DH- Paint Dry-Wall | [5 empty] | 17-May-25 |  | 20-May-25
CHI11-05-03-120 | C05/03-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 17-May-25 |  | 19-May-25
CHI11-05-03-125 | C05/03-Elec Rm- Paint Dry-Wall | [5 empty] | 19-May-25 |  | 20-May-25
CHI11-05-03-130 | C05/03-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 20-May-25 |  | 27-May-25
CHI11-05-03-135 | C05/03-DH- Install Screen Mesh + Caulking | [5 empty] | 21-May-25 |  | 23-May-25
CHI11-05-03-140 | C05/03-Elec Rm- General Cleaning | [5 empty] | 21-May-25 |  | 21-May-25
CHI11-05-03-145 | C05/03-Elec Rm- Set Electrical Equipments | [5 empty] | 22-May-25 |  | 27-May-25
CHI11-05-03-15 | C05/03-DH- Install Framing | [5 empty] | 02-May-25 |  | 06-May-25
CHI11-05-03-150 | C05/03-DH- Install Secondary Steel | [5 empty] | 27-May-25 |  | 27-May-25
CHI11-05-03-155 | C05/03-DH- Paint Secondary Steel | [5 empty] | 28-May-25 |  | 29-May-25
CHI11-05-03-160 | C05/03-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 28-May-25 |  | 03-Jun-25
CHI11-05-03-165 | C05/03-DH- General Cleaning | [5 empty] | 30-May-25 |  | 30-May-25
CHI11-05-03-170 | C05/03-DH- Install Ceiling Grid | [5 empty] | 30-May-25 |  | 03-Jun-25
CHI11-05-03-175 | C05/03-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 02-Jun-25 |  | 03-Jun-25
CHI11-05-03-180 | C05/03-DH- Install Perimeter Cable Trays | [5 empty] | 04-Jun-25 |  | 07-Jun-25
CHI11-05-03-185 | C05/03-DH- Assemble HACs [Qty - 5] | [5 empty] | 04-Jun-25 |  | 09-Jun-25
CHI11-05-03-190 | C05/03-Mech Gallery- Finish Dry-Wall | [5 empty] | 04-Jun-25 |  | 05-Jun-25
CHI11-05-03-195 | C05/03-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 04-Jun-25 |  | 04-Jun-25
CHI11-05-03-20 | C05/03-DH- In-Wall R/I | [5 empty] | 07-May-25 |  | 09-May-25
CHI11-05-03-200 | C05/03-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 05-Jun-25 |  | 09-Jun-25
CHI11-05-03-205 | C05/03-DH- Install Busways on HAC Arms | [5 empty] | 06-Jun-25 |  | 11-Jun-25
CHI11-05-03-210 | C05/03-Mech Gallery- Paint Dry-Wall | [5 empty] | 06-Jun-25 |  | 07-Jun-25
CHI11-05-03-215 | C05/03-DH- Install Device Tiles | [5 empty] | 09-Jun-25 |  | 10-Jun-25
CHI11-05-03-220 | C05/03-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 09-Jun-25 |  | 13-Jun-25
CHI11-05-03-225 | C05/03-DH- Set PDUs | [5 empty] | 09-Jun-25 |  | 12-Jun-25
CHI11-05-03-230 | C05/03-Mech Gallery- General Cleaning | [5 empty] | 09-Jun-25 |  | 11-Jun-25
CHI11-05-03-235 | C05/03-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 10-Jun-25 |  | 11-Jun-25
CHI11-05-03-240 | C05/03-Mech Gallery- Install BAS Equipments | [5 empty] | 10-Jun-25 |  | 21-Jun-25
CHI11-05-03-245 | C05/03-Mech Gallery- Set Mechanical Equipments | [5 empty] | 12-Jun-25 |  | 17-Jun-25
CHI11-05-03-25 | C05/03-Elec Rm- Install Framing | [5 empty] | 07-May-25 |  | 08-May-25
CHI11-05-03-250 | C05/03-DH- Raise HACs | [5 empty] | 16-Jun-25 |  | 19-Jun-25
CHI11-05-03-255 | C05/03-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 18-Jun-25 |  | 01-Jul-25
CHI11-05-03-260 | C05/03-DH- Detail HACs | [5 empty] | 20-Jun-25 |  | 24-Jun-25
CHI11-05-03-265 | C05/03-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 20-Jun-25 |  | 23-Jun-25
CHI11-05-03-270 | C05/03-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 23-Jun-25 |  | 01-Jul-25
CHI11-05-03-275 | C05/03-DH- Install Conduits PDU to Cable Trays | [5 empty] | 24-Jun-25 |  | 26-Jun-25
CHI11-05-03-280 | C05/03- Punchlist | [5 empty] | 09-Aug-25 |  | 21-Aug-25
CHI11-05-03-285 | C05/03-DH- Pull Feeders from PDUs to Busways | [5 empty] | 27-Jun-25 |  | 02-Jul-25
CHI11-05-03-290 | C05/03-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 02-Jul-25 |  | 08-Jul-25
CHI11-05-03-295 | C05/03-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | [5 empty] | 11-Jul-25 |  | 23-Jul-25
CHI11-05-03-30 | C05/03-Elec Rm- In-Wall R/I | [5 empty] | 09-May-25 |  | 10-May-25
CHI11-05-03-300 | C05/03-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 24-Jul-25 |  | 29-Jul-25
CHI11-05-03-305 | C05/03-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | [5 empty] | 24-Jul-25 |  | 05-Aug-25
CHI11-05-03-310 | C05/03-DH- Terminate PDUs | [5 empty] | 06-Aug-25 |  | 08-Aug-25
CHI11-05-03-315 | C05/03-L2Cx- Yellow Tags | [5 empty] | 09-Aug-25 |  | 03-Sep-25
CHI11-05-03-320 | C05/03-L3Cx- Control Power Checks | [5 empty] | 25-Aug-25 |  | 03-Sep-25
CHI11-05-03-325 | C05/03-L3Cx- EPMS Point to Point Checks | [5 empty] | 04-Sep-25 |  | 13-Sep-25
CHI11-05-03-330 | C05/03-L3Cx- FTE Energizations [480v] | [5 empty] | 15-Sep-25 |  | 19-Sep-25
CHI11-05-03-335 | C05/03-L3Cx- Startups | [5 empty] | 20-Sep-25 |  | 04-Oct-25
CHI11-05-03-340 | C05/03-L3Cx- Loadbanking | [5 empty] | 06-Oct-25 |  | 11-Oct-25
CHI11-05-03-35 | C05/03-DH- Overhead R/I - Fire Protection | [5 empty] | 10-May-25 |  | 13-May-25
CHI11-05-03-40 | C05/03-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 10-May-25 |  | 13-May-25
CHI11-05-03-45 | C05/03-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 12-May-25 |  | 13-May-25
CHI11-05-03-50 | C05/03-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 12-May-25 |  | 15-May-25
CHI11-05-03-55 | C05/03-DH- Overhead R/I - Fire Alarm | [5 empty] | 14-May-25 |  | 16-May-25
CHI11-05-03-60 | C05/03-DH- Overhead R/I - Electrical | [5 empty] | 14-May-25 |  | 17-May-25
CHI11-05-03-65 | C05/03-DH- Finish Dry-Wall | [5 empty] | 14-May-25 |  | 16-May-25
CHI11-05-03-70 | C05/03-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 14-May-25 |  | 15-May-25
CHI11-05-03-75 | C05/03-Elec Rm- Overhead R/I - Electrical | [5 empty] | 14-May-25 |  | 16-May-25
CHI11-05-03-80 | C05/03-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 14-May-25 |  | 15-May-25
CHI11-05-03-85 | C05/03-DH- Overhead R/I - Mechanical | [5 empty] | 16-May-25 |  | 17-May-25
CHI11-05-03-90 | C05/03-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 16-May-25 |  | 17-May-25
CHI11-05-03-95 | C05/03-Elec Rm- Finish Dry-Wall | [5 empty] | 16-May-25 |  | 17-May-25
CHI11-05-04-10 | C05/04-DH- Layout Framing | [5 empty] | 19-Apr-25 |  | 19-Apr-25
CHI11-05-04-100 | C05/04-Elec Rm- Drop Cable Tray [Hanging Rods] | [5 empty] | 05-May-25 |  | 05-May-25
CHI11-05-04-105 | C05/04-Mech Gallery- Overhead R/I - Fire Alarm | [5 empty] | 05-May-25 |  | 06-May-25
CHI11-05-04-110 | C05/04-Mech Gallery- Overhead R/I - Electrical | [5 empty] | 05-May-25 |  | 07-May-25
CHI11-05-04-115 | C05/04-DH- Paint Dry-Wall | [5 empty] | 06-May-25 |  | 08-May-25
CHI11-05-04-120 | C05/04-Elec Rm- Install Cable Trays / Pathways | [5 empty] | 06-May-25 |  | 07-May-25
CHI11-05-04-125 | C05/04-Elec Rm- Paint Dry-Wall | [5 empty] | 07-May-25 |  | 08-May-25
CHI11-05-04-130 | C05/04-Mech Gallery- Overhead R/I - Mechanical | [5 empty] | 08-May-25 |  | 14-May-25
CHI11-05-04-135 | C05/04-DH- Install Screen Mesh + Caulking | [5 empty] | 09-May-25 |  | 12-May-25
CHI11-05-04-140 | C05/04-Elec Rm- General Cleaning | [5 empty] | 09-May-25 |  | 09-May-25
CHI11-05-04-145 | C05/04-Elec Rm- Set Electrical Equipments | [5 empty] | 10-May-25 |  | 14-May-25
CHI11-05-04-15 | C05/04-DH- Install Framing | [5 empty] | 21-Apr-25 |  | 23-Apr-25
CHI11-05-04-150 | C05/04-DH- Install Secondary Steel | [5 empty] | 13-May-25 |  | 14-May-25
CHI11-05-04-155 | C05/04-DH- Paint Secondary Steel | [5 empty] | 15-May-25 |  | 16-May-25
CHI11-05-04-160 | C05/04-Mech Gallery- Overhead R/I - Plumbing | [5 empty] | 15-May-25 |  | 21-May-25
CHI11-05-04-165 | C05/04-DH- General Cleaning | [5 empty] | 17-May-25 |  | 17-May-25
CHI11-05-04-170 | C05/04-DH- Install Ceiling Grid | [5 empty] | 17-May-25 |  | 21-May-25
CHI11-05-04-175 | C05/04-Mech Gallery- Install Drywall [Mech Gallery] | [5 empty] | 20-May-25 |  | 21-May-25
CHI11-05-04-180 | C05/04-DH- Install Perimeter Cable Trays | [5 empty] | 22-May-25 |  | 27-May-25
CHI11-05-04-185 | C05/04-DH- Assemble HACs [Qty - 5] | [5 empty] | 22-May-25 |  | 28-May-25
CHI11-05-04-190 | C05/04-Mech Gallery- Finish Dry-Wall | [5 empty] | 22-May-25 |  | 23-May-25
CHI11-05-04-195 | C05/04-Mech Gallery- Drop Cable Tray [Hanging Rods] | [5 empty] | 22-May-25 |  | 22-May-25
CHI11-05-04-20 | C05/04-DH- In-Wall R/I | [5 empty] | 24-Apr-25 |  | 26-Apr-25
CHI11-05-04-200 | C05/04-Mech Gallery- Install Ceiling Grid + Device Tiles | [5 empty] | 23-May-25 |  | 28-May-25
CHI11-05-04-205 | C05/04-DH- Install Busways on HAC Arms | [5 empty] | 27-May-25 |  | 30-May-25
CHI11-05-04-210 | C05/04-Mech Gallery- Paint Dry-Wall | [5 empty] | 27-May-25 |  | 27-May-25
CHI11-05-04-215 | C05/04-DH- Install Device Tiles | [5 empty] | 28-May-25 |  | 29-May-25
CHI11-05-04-220 | C05/04-DH- Install Fiber Runner [ Cable Trays on HAC Arms] | [5 empty] | 28-May-25 |  | 02-Jun-25
CHI11-05-04-225 | C05/04-DH- Set PDUs | [5 empty] | 28-May-25 |  | 31-May-25
CHI11-05-04-230 | C05/04-Mech Gallery- General Cleaning | [5 empty] | 28-May-25 |  | 30-May-25
CHI11-05-04-235 | C05/04-Mech Gallery- Install Cable Trays / Pathways | [5 empty] | 29-May-25 |  | 30-May-25
CHI11-05-04-240 | C05/04-Mech Gallery- Install BAS Equipments | [5 empty] | 29-May-25 |  | 09-Jun-25
CHI11-05-04-245 | C05/04-Mech Gallery- Set Mechanical Equipments | [5 empty] | 31-May-25 |  | 04-Jun-25
CHI11-05-04-25 | C05/04-Elec Rm- Install Framing | [5 empty] | 24-Apr-25 |  | 25-Apr-25
CHI11-05-04-250 | C05/04-DH- Raise HACs | [5 empty] | 03-Jun-25 |  | 06-Jun-25
CHI11-05-04-255 | C05/04-Mech Gallery- Pull Cable to Mechanical Equipments [From Electrical Room] | [5 empty] | 05-Jun-25 |  | 19-Jun-25
CHI11-05-04-260 | C05/04-DH- Detail HACs | [5 empty] | 07-Jun-25 |  | 11-Jun-25
CHI11-05-04-265 | C05/04-DH- Connect Perimeter Cable Trays to HAC Cable Trays | [5 empty] | 07-Jun-25 |  | 10-Jun-25
CHI11-05-04-270 | C05/04-Mech Gallery- Pull & Terminate BAS Equipments | [5 empty] | 10-Jun-25 |  | 19-Jun-25
CHI11-05-04-275 | C05/04-DH- Install Conduits PDU to Cable Trays | [5 empty] | 11-Jun-25 |  | 13-Jun-25
CHI11-05-04-280 | C05/04-Elec Rm- Pull Cable between Elec Equipments [Inside Electrical Room] Pull Crew 2 | [5 empty] | 12-Jun-25 |  | 25-Jun-25
CHI11-05-04-285 | C05/04- Punchlist | [5 empty] | 15-Jul-25 |  | 25-Jul-25
CHI11-05-04-290 | C05/04-DH- Pull Feeders from PDUs to Busways | [5 empty] | 16-Jun-25 |  | 20-Jun-25
CHI11-05-04-295 | C05/04-Mech Gallery- Terminate Mechanical Equipments | [5 empty] | 20-Jun-25 |  | 24-Jun-25
CHI11-05-04-30 | C05/04-Elec Rm- In-Wall R/I | [5 empty] | 26-Apr-25 |  | 28-Apr-25
CHI11-05-04-300 | C05/04-Elec Rm- Terminate Electrical Equipments [Inside Electrical Room] | [5 empty] | 26-Jun-25 |  | 30-Jun-25
CHI11-05-04-305 | C05/04-Elec Rm- Pull Feeders from Electrical Room to PDUs Pull Crew 2 | [5 empty] | 26-Jun-25 |  | 10-Jul-25
CHI11-05-04-310 | C05/04-DH- Terminate PDUs | [5 empty] | 11-Jul-25 |  | 14-Jul-25
CHI11-05-04-315 | C05/04-L2Cx- Yellow Tags | [5 empty] | 15-Jul-25 |  | 07-Aug-25
CHI11-05-04-320 | C05/04-L3Cx- Control Power Checks | [5 empty] | 04-Aug-25 |  | 12-Aug-25
CHI11-05-04-325 | C05/04-L3Cx- EPMS Point to Point Checks | [5 empty] | 13-Aug-25 |  | 22-Aug-25
CHI11-05-04-330 | C05/04-L3Cx- FTE Energizations [480v] | [5 empty] | 23-Aug-25 |  | 27-Aug-25
CHI11-05-04-335 | C05/04-L3Cx- Startups | [5 empty] | 28-Aug-25 |  | 12-Sep-25
CHI11-05-04-340 | C05/04-L3Cx- Loadbanking | [5 empty] | 13-Sep-25 |  | 17-Sep-25
CHI11-05-04-35 | C05/04-DH- Overhead R/I - Fire Protection | [5 empty] | 28-Apr-25 |  | 30-Apr-25
CHI11-05-04-40 | C05/04-DH- Install Drywall (One Side - Facing DH) | [5 empty] | 28-Apr-25 |  | 30-Apr-25
CHI11-05-04-45 | C05/04-Elec Rm- Overhead R/I - Fire Protection | [5 empty] | 29-Apr-25 |  | 30-Apr-25
CHI11-05-04-50 | C05/04-Elec Rm- Install Drywall [Elec + Battery Rooms] | [5 empty] | 29-Apr-25 |  | 02-May-25
CHI11-05-04-55 | C05/04-DH- Overhead R/I - Fire Alarm | [5 empty] | 01-May-25 |  | 05-May-25
CHI11-05-04-60 | C05/04-DH- Overhead R/I - Electrical | [5 empty] | 01-May-25 |  | 06-May-25
CHI11-05-04-65 | C05/04-DH- Finish Dry-Wall | [5 empty] | 01-May-25 |  | 05-May-25
CHI11-05-04-70 | C05/04-Elec Rm- Overhead R/I - Fire Alarm | [5 empty] | 01-May-25 |  | 02-May-25
CHI11-05-04-75 | C05/04-Elec Rm- Overhead R/I - Electrical | [5 empty] | 01-May-25 |  | 05-May-25
CHI11-05-04-80 | C05/04-Mech Gallery- Overhead R/I - Fire Protection | [5 empty] | 01-May-25 |  | 02-May-25
CHI11-05-04-85 | C05/04-DH- Overhead R/I - Mechanical | [5 empty] | 05-May-25 |  | 06-May-25
CHI11-05-04-90 | C05/04-DH- Drop Cable Tray [Hanging Rods] | [5 empty] | 05-May-25 |  | 06-May-25
CHI11-05-04-95 | C05/04-Elec Rm- Finish Dry-Wall | [5 empty] | 05-May-25 |  | 06-May-25
CHI11-05-C&S-10 | C05- Install Primary Steel | [5 empty] | 12-Nov-2024 |  | 03-Dec-24
CHI11-05-C&S-15 | C05- Install Roof Panels | [5 empty] | 02-Jan-25 |  | 15-Jan-25
CHI11-05-C&S-20 | C05- UG MEP Work AMS/Gibson | [5 empty] | 17-Dec-24 |  | 13-Jan-25
CHI11-05-C&S-25 | C05- Install Exterior Wall Panels | [5 empty] | 04-Dec-24 |  | 31-Dec-24
CHI11-05-C&S-30 | C05- Prep / Place SOG | [5 empty] | 14-Jan-25 |  | 25-Jan-25
CHI11-05-C&S-35 | C05- Install Louvers & Dampers | [5 empty] | 27-Jan-25 |  | 14-Feb-25
CHI11-05-C&S-40 | C05- Install Misc. Metals (Trims, Gutters, Catwalks) | [5 empty] | 27-Jan-25 |  | 14-Feb-25
CHI11-05-L4-10 | C05-L4Cx- Testing <MSFT Duration> | [5 empty] | 17-Oct-25 |  | 15-Nov-25
CHI11-05-L5-10 | C05-L5Cx- Testing <MSFT Duration> | [5 empty] | 17-Nov-25 |  | 19-Nov-25
CHI11-05-YARD-10 | C05/Yard- Build Equipment Pads for XFMs | [5 empty] | 28-Mar-25 |  | 07-Apr-25
CHI11-05-YARD-15 | C05/Yard- Build Equipment Pads for UPMs | [5 empty] | 08-Apr-25 |  | 18-Apr-25
CHI11-05-YARD-20 | C05/Yard- Build Equipment Pads for UMSs | [5 empty] | 19-Apr-25 |  | 29-Apr-25
CHI11-05-YARD-25 | C05/Yard- Build Equipment Pads for Generators | [5 empty] | 30-Apr-25 |  | 10-May-25
CHI11-05-YARD-30 | C05/Yard- MV Cable Pulling & Terminating(To Junction Box) to Cell 1 | [5 empty] | 02-May-25 |  | 12-May-25
CHI11-05-YARD-35 | C05/Yard- Install XFMs | [5 empty] | 12-May-25 |  | 23-May-25
CHI11-05-YARD-40 | C05/Yard- MV Cable Pulling & Terminating(To Junction Box) to Cell 2 | [5 empty] | 13-May-25 |  | 21-May-25
CHI11-05-YARD-45 | C05/Yard- Install UPMs | [5 empty] | 14-May-25 |  | 27-May-25
CHI11-05-YARD-50 | C05/Yard- Install UMSs | [5 empty] | 16-May-25 |  | 29-May-25
CHI11-05-YARD-55 | C05/Yard- Install Generators | [5 empty] | 19-May-25 |  | 31-May-25
CHI11-05-YARD-60 | C05/Yard- MV Cable Pulling & Terminating(To Junction Box) to Cell 4 | [5 empty] | 22-May-25 |  | 31-May-25
CHI11-05-YARD-65 | C05/Yard- Terminate MV Gear - Cell 1 |  |  |  | CELL1 |  | 30-May-25 |  | 03-Jun-25
CHI11-05-YARD-70 | C05/Yard- MV Cable Pulling & Terminating(To Junction Box) to Cell 3 | [5 empty] | 02-Jun-25 |  | 10-Jun-25
CHI11-05-YARD-75 | C05/Yard- Terminate MV Gear - Cell 2 |  |  |  | CELL2 |  | 04-Jun-25 |  | 07-Jun-25
CHI11-05-YARD-80 | C05/Yard- Terminate MV Gear - Cell 4 |  |  |  | CELL4 |  | 09-Jun-25 |  | 12-Jun-25
CHI11-05-YARD-85 | C05/Yard- Terminate MV Gear - Cell 3 |  |  |  | CELL3 |  | 13-Jun-25 |  | 18-Jun-25
CHI11-ADMIN-10 | Admin/Elec Rm- Fire Protection OH R/I | [5 empty] | 20-Jan-25 |  | 20-Jan-25
CHI11-ADMIN-100 | Admin/ Fire Riser Rm- Fire Protection OH R/I | [5 empty] | 27-Jan-25 |  | 27-Jan-25
CHI11-ADMIN-105 | Admin/ Elec Rm- Finsh Drywall and Wall Protection | [5 empty] | 28-Jan-25 |  | 31-Jan-25
CHI11-ADMIN-110 | Admin/ Fire Riser Rm- Framing | [5 empty] | 28-Jan-25 |  | 28-Jan-25
CHI11-ADMIN-115 | Admin/ Other- Fire Protection OH R/I | [5 empty] | 28-Jan-25 |  | 28-Jan-25
CHI11-ADMIN-120 | Admin/ Ent Rm-01- Secondary / Ceiling Steel | [5 empty] | 29-Jan-25 |  | 29-Jan-25
CHI11-ADMIN-125 | Admin/ Ent Rm-02- Top Out Drywall - Ceiling Steel Height | [5 empty] | 29-Jan-25 |  | 30-Jan-25
CHI11-ADMIN-130 | ADMIN/ FCR- MEP Rough-In & OH | [5 empty] | 29-Jan-25 |  | 30-Jan-25
CHI11-ADMIN-135 | Admin/ Other- Framing | [5 empty] | 29-Jan-25 |  | 29-Jan-25
CHI11-ADMIN-140 | Admin/ Loading Dock- Fire Protection OH R/I | [5 empty] | 29-Jan-25 |  | 29-Jan-25
CHI11-ADMIN-145 | Admin/ Fire Riser Rm- Install Duct Work | [5 empty] | 29-Jan-25 |  | 30-Jan-25
CHI11-ADMIN-15 | Admin/ Elec Rm- Framing | [5 empty] | 21-Jan-25 |  | 21-Jan-25
CHI11-ADMIN-150 | Admin/ Loading Dock- Install Ductwork | [5 empty] | 29-Jan-25 |  | 15-Feb-25
CHI11-ADMIN-155 | Admin/ Ent Rm-01- Finsh Drywall and Wall Protection | [5 empty] | 30-Jan-25 |  | 03-Feb-25
CHI11-ADMIN-160 | Admin/ Loading Dock- Install Ductwork (Remaining Rooms, Corridor) | [5 empty] | 30-Jan-25 |  | 17-Feb-25
CHI11-ADMIN-165 | Admin/ Loading Dock- Framing | [5 empty] | 30-Jan-25 |  | 30-Jan-25
CHI11-ADMIN-170 | Admin/ Ent Rm-02- Secondary / Ceiling Steel | [5 empty] | 31-Jan-25 |  | 31-Jan-25
CHI11-ADMIN-175 | ADMIN/ FCR- Top Out Drywall - Ceiling Steel Height | [5 empty] | 31-Jan-25 |  | 01-Feb-25
CHI11-ADMIN-180 | ADMIN/ SER- MEP Rough-In & OH | [5 empty] | 31-Jan-25 |  | 01-Feb-25
CHI11-ADMIN-185 | Admin/ Loading Dock- Rough-in | [5 empty] | 31-Jan-25 |  | 31-Jan-25
CHI11-ADMIN-190 | Admin/ Fire Riser Rm- Install downcomers | [5 empty] | 31-Jan-25 |  | 31-Jan-25
CHI11-ADMIN-195 | Admin/ Ent Rm-02- Finsh Drywall and Wall Protection | [5 empty] | 01-Feb-25 |  | 05-Feb-25
CHI11-ADMIN-20 | Admin/ Ent Rm-01- Fire Protection OH R/I | [5 empty] | 21-Jan-25 |  | 21-Jan-25
CHI11-ADMIN-200 | Admin/ Elec Rm- Paint | [5 empty] | 01-Feb-25 |  | 03-Feb-25
CHI11-ADMIN-205 | ADMIN/ FCR- Secondary / Ceiling Steel | [5 empty] | 03-Feb-25 |  | 03-Feb-25
CHI11-ADMIN-210 | ADMIN/ SER- Top Out Drywall - Ceiling Steel Height | [5 empty] | 03-Feb-25 |  | 04-Feb-25
CHI11-ADMIN-215 | Admin/ High Value Rm- MEP Rough-In & OH | [5 empty] | 03-Feb-25 |  | 04-Feb-25
CHI11-ADMIN-220 | Admin/ Elec Rm- Cable Tray / Ceiling Steel Height | [5 empty] | 04-Feb-25 |  | 04-Feb-25
CHI11-ADMIN-225 | ADMIN/ FCR- Finsh Drywall and Wall Protection | [5 empty] | 04-Feb-25 |  | 07-Feb-25
CHI11-ADMIN-230 | Admin/ Elec Rm- Set Electrical Equipment in Admin | [5 empty] | 03-Mar-25 |  | 11-Mar-25
CHI11-ADMIN-235 | Admin/ Ent Rm-01- Paint | [5 empty] | 04-Feb-25 |  | 05-Feb-25
CHI11-ADMIN-240 | ADMIN/ SER- Secondary / Ceiling Steel | [5 empty] | 05-Feb-25 |  | 05-Feb-25
CHI11-ADMIN-245 | Admin/ High Value Rm- Top Out Drywall - Ceiling Steel Height | [5 empty] | 05-Feb-25 |  | 06-Feb-25
CHI11-ADMIN-25 | Admin/ Elec Rm- MEP Rough-In & OH | [5 empty] | 22-Jan-25 |  | 23-Jan-25
CHI11-ADMIN-250 | Admin/ Fire Riser Rm- MEP Rough-In & OH | [5 empty] | 05-Feb-25 |  | 06-Feb-25
CHI11-ADMIN-255 | ADMIN/ SER- Finsh Drywall | [5 empty] | 06-Feb-25 |  | 07-Feb-25
CHI11-ADMIN-260 | Admin/ Ent Rm-01- Install Raceway | [5 empty] | 06-Feb-25 |  | 10-Feb-25
CHI11-ADMIN-265 | Admin/ Ent Rm-02- Paint | [5 empty] | 06-Feb-25 |  | 07-Feb-25
CHI11-ADMIN-270 | Admin/ High Value Rm- Install Ductwork and Cracs | [5 empty] | 07-Feb-25 |  | 25-Feb-25
CHI11-ADMIN-275 | Admin/ Fire Riser Rm- Top Out Drywall - Ceiling Steel Height | [5 empty] | 07-Feb-25 |  | 10-Feb-25
CHI11-ADMIN-280 | Admin/ Other- MEP Rough-In & OH | [5 empty] | 07-Feb-25 |  | 10-Feb-25
CHI11-ADMIN-285 | Admin/ Ent Rm-02- Install Raceway | [5 empty] | 10-Feb-25 |  | 12-Feb-25
CHI11-ADMIN-290 | ADMIN/ FCR- Paint | [5 empty] | 10-Feb-25 |  | 11-Feb-25
CHI11-ADMIN-295 | ADMIN/ SER- Paint | [5 empty] | 10-Feb-25 |  | 11-Feb-25
CHI11-ADMIN-30 | Admin/ Ent Rm-01- Framing | [5 empty] | 22-Jan-25 |  | 22-Jan-25
CHI11-ADMIN-300 | Admin/ Fire Riser Rm- Secondary / Ceiling Steel | [5 empty] | 11-Feb-25 |  | 11-Feb-25
CHI11-ADMIN-305 | Admin/ Other- Top Out Drywall - Ceiling Steel Height | [5 empty] | 11-Feb-25 |  | 12-Feb-25
CHI11-ADMIN-310 | Admin/ Ent Rm-01- Set ER-1 Equipment | [5 empty] | 11-Feb-25 |  | 14-Feb-25
CHI11-ADMIN-315 | Admin/ Loading Dock- MEP Rough-In & OH | [5 empty] | 11-Feb-25 |  | 12-Feb-25
CHI11-ADMIN-320 | Admin/ Fire Riser Rm- Finsh Drywall | [5 empty] | 12-Feb-25 |  | 13-Feb-25
CHI11-ADMIN-325 | ADMIN/ FCR- Install Raceway | [5 empty] | 12-Feb-25 |  | 14-Feb-25
CHI11-ADMIN-330 | ADMIN/ SER- Install Raceway | [5 empty] | 12-Feb-25 |  | 14-Feb-25
CHI11-ADMIN-335 | Admin/ Other- Finsh Drywall | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-ADMIN-340 | Admin/ Loading Dock- Top Out Drywall - Ceiling Steel Height | [5 empty] | 13-Feb-25 |  | 14-Feb-25
CHI11-ADMIN-345 | Admin/ Ent Rm-02- Set ER-2 Equipment | [5 empty] | 13-Feb-25 |  | 17-Feb-25
CHI11-ADMIN-35 | Admin/ Ent Rm-02- Fire Protection OH R/I | [5 empty] | 22-Jan-25 |  | 22-Jan-25
CHI11-ADMIN-350 | Admin/ Fire Riser Rm- Paint | [5 empty] | 14-Feb-25 |  | 15-Feb-25
CHI11-ADMIN-355 | Admin/ Elec Rm- Pull Feeders to Admin | [5 empty] | 12-Mar-25 |  | 28-Mar-25
CHI11-ADMIN-360 | Admin/ Other- Paint | [5 empty] | 15-Feb-25 |  | 17-Feb-25
CHI11-ADMIN-365 | Admin/ Loading Dock- Finsh Drywall | [5 empty] | 15-Feb-25 |  | 17-Feb-25
CHI11-ADMIN-370 | ADMIN/ SER- Set SER Room Equipment | [5 empty] | 15-Feb-25 |  | 19-Feb-25
CHI11-ADMIN-375 | ADMIN/ FCR- Set FCR Equipment | [5 empty] | 15-Feb-25 |  | 19-Feb-25
CHI11-ADMIN-380 | Admin/ Fire Riser Rm- Ceiling Grid & Tile | [5 empty] | 18-Feb-25 |  | 21-Feb-25
CHI11-ADMIN-385 | Admin/ Other- Ceiling Grid & Tile | [5 empty] | 18-Feb-25 |  | 21-Feb-25
CHI11-ADMIN-390 | Admin/ Loading Dock- Paint | [5 empty] | 18-Feb-25 |  | 19-Feb-25
CHI11-ADMIN-395 | ADMIN/ FCR- Pull Fiber For EPMS VLAN | [5 empty] | 20-Feb-25 |  | 06-Mar-25
CHI11-ADMIN-40 | Admin/ Ent Rm-02- Framing | [5 empty] | 23-Jan-25 |  | 23-Jan-25
CHI11-ADMIN-400 | ADMIN/ FCR- Pull Copper for EPMS VLAN | [5 empty] | 20-Feb-25 |  | 06-Mar-25
CHI11-ADMIN-405 | Admin/ Loading Dock- Plumbing | [5 empty] | 20-Feb-25 |  | 10-Mar-25
CHI11-ADMIN-410 | ADMIN- Install Doors | [5 empty] | 22-Feb-25 |  | 26-Feb-25
CHI11-ADMIN-415 | Admin/ Fire Riser Rm- Complete Pipe/ Valves | [5 empty] | 22-Feb-25 |  | 24-Feb-25
CHI11-ADMIN-420 | Admin/ High Value Rm- Finsh Drywall | [5 empty] | 26-Feb-25 |  | 03-Mar-25
CHI11-ADMIN-425 | ADMIN- Light Fixtures Installation | [5 empty] | 27-Feb-25 |  | 11-Mar-25
CHI11-ADMIN-430 | Admin/ High Value Rm- Paint | [5 empty] | 04-Mar-25 |  | 05-Mar-25
CHI11-ADMIN-435 | Admin/ Elec Rm- Pull Branches From Admin | [5 empty] | 29-Mar-25 |  | 11-Apr-25
CHI11-ADMIN-440 | Admin/ High Value Rm- Fit-out | [5 empty] | 06-Mar-25 |  | 17-Mar-25
CHI11-ADMIN-445 | ADMIN/ FCR- Pull Fiber For Tahuya VLAN | [5 empty] | 07-Mar-25 |  | 20-Mar-25
CHI11-ADMIN-45 | ADMIN/ FCR- Fire Protection OH R/I | [5 empty] | 23-Jan-25 |  | 23-Jan-25
CHI11-ADMIN-450 | ADMIN/ FCR- Pull Copper for Tahuya VLAN | [5 empty] | 07-Mar-25 |  | 20-Mar-25
CHI11-ADMIN-455 | Admin/ Loading Dock- Pull Cables | [5 empty] | 11-Mar-25 |  | 13-Mar-25
CHI11-ADMIN-460 | Admin/ Elec Rm- Terminate Electrical / Mechanical Equipment | [5 empty] | 14-Apr-25 |  | 17-Apr-25
CHI11-ADMIN-465 | ADMIN/ FCR- Pull Fiber For BAS VLAN | [5 empty] | 21-Mar-25 |  | 04-Apr-25
CHI11-ADMIN-470 | ADMIN/ FCR- Pull Copper for BAS VLAN | [5 empty] | 21-Mar-25 |  | 04-Apr-25
CHI11-ADMIN-475 | ADMIN/ FCR- Pull Fiber/Copper For CORPNET Network | [5 empty] | 05-Apr-25 |  | 19-Apr-25
CHI11-ADMIN-480 | ADMIN/ FCR- Pull Fiber For CEI Network | [5 empty] | 21-Apr-25 |  | 05-May-25
CHI11-ADMIN-485 | Admin - Beneficial Rooms PunchList | [5 empty] | 06-May-25 |  | 09-May-25
CHI11-ADMIN-490 | ADMIN- Remaining Area Punchlist | [5 empty] | 12-Mar-25 |  | 17-Mar-25
CHI11-ADMIN-50 | Admin/ Elec Rm- Top Out Drywall - Ceiling Steel Height | [5 empty] | 24-Jan-25 |  | 25-Jan-25
CHI11-ADMIN-55 | Admin/ Ent Rm-01- MEP Rough-In & OH | [5 empty] | 24-Jan-25 |  | 25-Jan-25
CHI11-ADMIN-60 | ADMIN/ FCR- Framing | [5 empty] | 24-Jan-25 |  | 24-Jan-25
CHI11-ADMIN-65 | ADMIN/ SER- Fire Protection OH R/I | [5 empty] | 24-Jan-25 |  | 24-Jan-25
CHI11-ADMIN-70 | ADMIN/ SER- Framing | [5 empty] | 25-Jan-25 |  | 25-Jan-25
CHI11-ADMIN-75 | Admin/ High Value Rm- Fire Protection OH R/I | [5 empty] | 25-Jan-25 |  | 25-Jan-25
CHI11-ADMIN-80 | Admin/ Elec Rm- Secondary / Ceiling Steel | [5 empty] | 27-Jan-25 |  | 27-Jan-25
CHI11-ADMIN-85 | Admin/ Ent Rm-01- Top Out Drywall - Ceiling Steel Height | [5 empty] | 27-Jan-25 |  | 28-Jan-25
CHI11-ADMIN-90 | Admin/ Ent Rm-02- MEP Rough-In & OH | [5 empty] | 27-Jan-25 |  | 28-Jan-25
CHI11-ADMIN-95 | Admin/ High Value Rm- Framing | [5 empty] | 27-Jan-25 |  | 27-Jan-25
CHI11-BIM-10 | BIM- BIM Kickoff | [5 empty] | 18-Jul-2024
CHI11-BIM-15 | BIM- UG BIM Co-ordination | [5 empty] | 19-Jul-2024 |  | 26-Sep-2024
CHI11-BIM-20 | BIM- Above ground BIM Co-ordination | [5 empty] | 27-Sep-2024 |  | 23-Dec-24
CHI11-FDN-10 | Foundations / Stem Walls (50% Complete) | [5 empty] | 19-Sep-2024 |  | 09-Oct-2024
CHI11-FDN-15 | Foundations / Stem Walls (100% Complete) | [5 empty] | 10-Oct-2024 |  | 12-Nov-2024
CHI11-MOB-10 | Site Mobilization | [5 empty] | 24-Jul-2024
CHI11-MOB-15 | Set-Up Trailers & Install Temp Utilities | [5 empty] | 25-Jul-2024 |  | 16-Sep-2024
CHI11-MOB-20 | Fine Grading Building Pad | [5 empty] | 19-Aug-2024 |  | 04-Sep-2024
CHI11-PROC-10 | PROCUREMENT- ARL & Subcontractor Awards | [5 empty] | 07-Jun-2024 |  | 07-Sep-2024
CHI11-PROC-15 | PROCUREMENT- Buyouts & Early Procurement | [5 empty] | 07-Jun-2024 |  | 30-Sep-2024
CHI11-RFP-10 | RFP- RFP Issued (Revised 3.21.24) and Proposal Due to MSFT | [5 empty] | 25-Mar-2024 |  | 12-Apr-2024
CHI11-RFP-15 | RFP- Microsoft Reviews Proposals | [5 empty] | 15-Apr-2024 |  | 03-May-2024
CHI11-RFP-20 | RFP- Microsoft Awards CHI11 | [5 empty] | 06-May-2024 |  | 05-Jun-2024
CHI11-RFP-25 | RFP- PSR Executed (Early Works) | [5 empty] | 06-Jun-2024 |  | 06-Jun-2024
CHI11-RFP-30 | RFP- PSR Executed (Full GMP) | [5 empty] | 30-Sep-2024 |  | 30-Sep-2024
CHI11-SU-10 | Install Deep Telecom | [5 empty] | 08-Oct-2024 |  | 14-Nov-2024
CHI11-SU-15 | Install MV Ductbanks | [5 empty] | 25-Oct-2024 |  | 22-Nov-24
CHI11-SU-20 | Install UG Telecom (under Building Pad) | [5 empty] | 08-Oct-2024 |  | 10-Oct-2024
CHI11-SU-25 | Install UG Electrical / UPM Crossing (under Building Pad) | [5 empty] | 25-Oct-2024 |  | 13-Nov-2024
CHI11-SU-30 | Install Storm Lines | [5 empty] | 09-Oct-2024 |  | 06-Dec-24
CHI11-SU-35 | Install Sanitary Lines | [5 empty] | 04-Nov-2024 |  | 09-Dec-24
CHI11-SU-40 | Install Water Line | [5 empty] | 04-Nov-2024 |  | 26-Dec-24
CHI11-SU-45 | Backfill after UG work (MV / Telecom) | [5 empty] | 05-Nov-2024 |  | 15-Nov-2024
CHI11-SU-50 | Permanent Power (Need by Date) | [5 empty] | 05-May-25
CHI11_WeeklyUpdate_BL1-0_2024-11-15 | [6 empty] | 25-Mar-2024 |  | 22-Jan-26
COLO 3 | [6 empty] | 09-Apr-2024 |  | 13-Mar-25
COLO 3 - CELL 1 | [6 empty] | 17-Jan-25 |  | 28-Apr-25
COLO 3 - CELL 1 Data Hall | [6 empty] | 17-Jan-25 |  | 16-Apr-25
COLO 3 - CELL 1 Electrical Room | [6 empty] | 25-Jan-25 |  | 11-Apr-25
COLO 3 - CELL 1 Mechanical Gallery | [6 empty] | 13-Feb-25 |  | 07-Apr-25
COLO 3 - CELL 2 | [6 empty] | 29-Jan-25 |  | 23-May-25
COLO 3 - CELL 2 Data Hall | [6 empty] | 29-Jan-25 |  | 12-May-25
COLO 3 - CELL 2 Electrical Room | [6 empty] | 03-Feb-25 |  | 08-May-25
COLO 3 - CELL 2 Mechanical Gallery | [6 empty] | 11-Feb-25 |  | 04-Apr-25
COLO 3 - CELL 2 Punchlist | [6 empty] | 13-May-25 |  | 23-May-25
COLO 3 - CELL 3 | [6 empty] | 21-Feb-25 |  | 20-Jun-25
COLO 3 - CELL 3 Data Hall | [6 empty] | 21-Feb-25 |  | 07-Jun-25
COLO 3 - CELL 3 Electrical Room | [6 empty] | 26-Feb-25 |  | 04-Jun-25
COLO 3 - CELL 3 Mechanical Gallery | [6 empty] | 06-Mar-25 |  | 28-Apr-25
COLO 3 - CELL 3 Punchlist | [6 empty] | 09-Jun-25 |  | 20-Jun-25
COLO 3 - CELL 4 | [6 empty] | 10-Feb-25 |  | 21-May-25
COLO 3 - CELL 4 Data Hall | [6 empty] | 10-Feb-25 |  | 13-May-25
COLO 3 - CELL 4 Electrical Room | [6 empty] | 14-Feb-25 |  | 09-May-25
COLO 3 - CELL 4 Mechanical Gallery | [6 empty] | 21-Feb-25 |  | 16-Apr-25
COLO 3 - CELL 4 Punchlist | [6 empty] | 10-May-25 |  | 21-May-25
COLO 3- CELL 1 Punchlist | [6 empty] | 17-Apr-25 |  | 28-Apr-25
COLO 4 | [6 empty] | 02-Sep-2024 |  | 06-Nov-25
COLO 4 - CELL 1 | [6 empty] | 24-Feb-25 |  | 16-May-25
COLO 4 - CELL 1 Data Hall | [6 empty] | 24-Feb-25 |  | 05-May-25
COLO 4 - CELL 1 Electrical Room | [6 empty] | 28-Feb-25 |  | 30-Apr-25
COLO 4 - CELL 1 Mechanical Gallery | [6 empty] | 08-Mar-25 |  | 30-Apr-25
COLO 4 - CELL 1 Punchlist | [6 empty] | 06-May-25 |  | 16-May-25
COLO 4 - CELL 2 | [6 empty] | 05-Mar-25 |  | 11-Jun-25
COLO 4 - CELL 2 Data Hall | [6 empty] | 05-Mar-25 |  | 30-May-25
COLO 4 - CELL 2 Electrical Room | [6 empty] | 10-Mar-25 |  | 27-May-25
COLO 4 - CELL 2 Mechanical Gallery | [6 empty] | 17-Mar-25 |  | 09-May-25
COLO 4 - CELL 2 Punchlist | [6 empty] | 31-May-25 |  | 11-Jun-25
COLO 4 - CELL 3 | [6 empty] | 28-Mar-25 |  | 02-Aug-25
COLO 4 - CELL 3 Data Hall | [6 empty] | 28-Mar-25 |  | 21-Jul-25
COLO 4 - CELL 3 Electrical Room | [6 empty] | 02-Apr-25 |  | 19-Jul-25
COLO 4 - CELL 3 Mechanical Gallery | [6 empty] | 09-Apr-25 |  | 02-Jun-25
COLO 4 - CELL 3 Punchlist | [6 empty] | 22-Jul-25 |  | 02-Aug-25
COLO 4 - CELL 4 | [6 empty] | 15-Mar-25 |  | 10-Jul-25
COLO 4 - CELL 4 Data Hall | [6 empty] | 15-Mar-25 |  | 26-Jun-25
COLO 4 - CELL 4 Electrical Room | [6 empty] | 20-Mar-25 |  | 23-Jun-25
COLO 4 - CELL 4 Mechanical Gallery | [6 empty] | 28-Mar-25 |  | 20-May-25
COLO 4 - CELL 4 Punchlist | [6 empty] | 27-Jun-25 |  | 10-Jul-25
COLO 5 | [6 empty] | 02-Sep-2024 |  | 04-Dec-25
COLO 5 - CELL 1 | [6 empty] | 31-Mar-25 |  | 17-Jun-25
COLO 5 - CELL 1 Data Hall | [6 empty] | 31-Mar-25 |  | 04-Jun-25
COLO 5 - CELL 1 Electrical Room | [6 empty] | 04-Apr-25 |  | 29-May-25
COLO 5 - CELL 1 Mechanical Gallery | [6 empty] | 11-Apr-25 |  | 04-Jun-25
COLO 5 - CELL 1 Punchlist | [6 empty] | 05-Jun-25 |  | 17-Jun-25
COLO 5 - CELL 2 | [6 empty] | 08-Apr-25 |  | 11-Jul-25
COLO 5 - CELL 2 Data Hall | [6 empty] | 08-Apr-25 |  | 27-Jun-25
COLO 5 - CELL 2 Electrical Room | [6 empty] | 14-Apr-25 |  | 24-Jun-25
COLO 5 - CELL 2 Mechanical Gallery | [6 empty] | 21-Apr-25 |  | 12-Jun-25
COLO 5 - CELL 2 Punchlist | [6 empty] | 28-Jun-25 |  | 11-Jul-25
COLO 5 - CELL 3 | [6 empty] | 01-May-25 |  | 21-Aug-25
COLO 5 - CELL 3 Data Hall | [6 empty] | 01-May-25 |  | 08-Aug-25
COLO 5 - CELL 3 Electrical Room | [6 empty] | 07-May-25 |  | 05-Aug-25
COLO 5 - CELL 3 Mechanical Gallery | [6 empty] | 14-May-25 |  | 08-Jul-25
COLO 5 - CELL 3 Punchlist | [6 empty] | 09-Aug-25 |  | 21-Aug-25
COLO 5 - CELL 4 | [6 empty] | 19-Apr-25 |  | 25-Jul-25
COLO 5 - CELL 4 Data Hall Fitout Activities | [6 empty] | 19-Apr-25 |  | 14-Jul-25
COLO 5 - CELL 4 Electrical Room | [6 empty] | 24-Apr-25 |  | 10-Jul-25
COLO 5 - CELL 4 Mechanical Gallery | [6 empty] | 01-May-25 |  | 24-Jun-25
COLO 5 - CELL 4 Punchlist | [6 empty] | 15-Jul-25 |  | 25-Jul-25
Clayco Key Milestones | [6 empty] | 19-Aug-2024 |  | 22-Jan-26
Commissioning | [6 empty] | 09-Apr-25 |  | 18-Sep-25
Commissioning (L2- L5) | [6 empty] | 05-May-25 |  | 19-Nov-25
Construction | [6 empty] | 24-Jul-2024 |  | 19-Nov-25
Core & Shell | [6 empty] | 14-Oct-2024 |  | 14-Feb-25
Core & Shell/ Fitout | [6 empty] | 02-Sep-2024 |  | 15-Mar-25
Div 01 Milestones | [6 empty] | 12-Apr-2024 |  | 04-Dec-25
Early Awards | [6 empty] | 07-Jun-2024 |  | 30-Sep-2024
Elec Performance Monitoring System | [6 empty] | 15-Nov-24 |  | 23-Feb-25
Electrical Room | [6 empty] | 20-Jan-25 |  | 17-Apr-25
Electrical Yard | [6 empty] | 17-Jan-25 |  | 18-Jun-25
Energizations & Startups (Level 3) | [6 empty] | 04-Jun-25 |  | 14-Aug-25
Entry Room 1 | [6 empty] | 21-Jan-25 |  | 14-Feb-25
Entry Room 2 | [6 empty] | 22-Jan-25 |  | 17-Feb-25
FCR (Facilities Control Room) | [6 empty] | 23-Jan-25 |  | 05-May-25
Fire Riser Room | [6 empty] | 27-Jan-25 |  | 24-Feb-25
Fitout | [6 empty] | 17-Jan-25 |  | 21-Aug-25
Foundations | [6 empty] | 19-Sep-2024 |  | 12-Nov-2024
Functional Testing (Level 4 & 5) | [6 empty] | 15-Aug-25 |  | 18-Sep-25
General | [6 empty] | 12-Apr-2024 |  | 19-Nov-25
HAC/Racking | [6 empty] | 15-Nov-24 |  | 21-Feb-25
LV Switchgear | [6 empty] | 28-Feb-25 |  | 04-Mar-25
Loading Dock | [6 empty] | 29-Jan-25 |  | 13-Mar-25
MSFT OFCI ROJ Dates | [6 empty] | 09-Apr-2024 |  | 15-May-25
Main LV Switch Board | [6 empty] | 08-Mar-25 |  | 08-Mar-25
Medium Voltage Switchgear | [6 empty] | 15-Oct-2024 |  | 23-Feb-25
Milestones | [6 empty] | 12-Apr-2024 |  | 22-Jan-26
Overall | [6 empty] | 08-Oct-2024 |  | 05-May-25
PEMB Procurement (1st Del) | [6 empty] | 14-Oct-2024 |  | 14-Oct-2024
Packaged Diesel Generator Set | [6 empty] | 15-Nov-24 |  | 24-Feb-25
Pad Mounted Transformers | [6 empty] | 15-Nov-24 |  | 23-Feb-25
Power Distribution Units | [6 empty] | 15-Nov-24 |  | 23-Feb-25
Preconstruction | [6 empty] | 25-Mar-2024 |  | 23-Dec-24
Procurement | [6 empty] | 09-Apr-2024 |  | 21-Nov-25
Punchlist | [6 empty] | 06-May-25 |  | 09-May-25
RFP / PSR | [6 empty] | 25-Mar-2024 |  | 30-Sep-2024
Remaining Rooms | [6 empty] | 27-Jan-25 |  | 17-Mar-25
Restrooms & Janitor Room | [6 empty] | 28-Jan-25 |  | 21-Feb-25
SER (Security Equipment Room) | [6 empty] | 24-Jan-25 |  | 19-Feb-25
STORAGE (High Value & Secure) Rooms | [6 empty] | 25-Jan-25 |  | 17-Mar-25
Site Prep/ Mobilization | [6 empty] | 24-Jul-2024 |  | 16-Sep-2024
Site Utilities | [6 empty] | 08-Oct-2024 |  | 05-May-25
UPS System W / Battery | [6 empty] | 02-Sep-2024 |  | 23-Feb-25
Under Building Pad | [6 empty] | 08-Oct-2024 |  | 15-Nov-2024
Utility Pad Mount Switchgear | [6 empty] | 23-Oct-2024 |  | 28-Feb-25
Yellow Tags (Level 2) | [6 empty] | 05-May-25 |  | 02-Jul-25